Process for conducting conditions assessment of the existing structural and/or nonstructural component configuration, quality of construction, physical condition, and interconnection to other structural components

The conditions assessment of the existing structural and/or nonstructural component configuration, quality of construction, physical condition, and interconnection to other structural components (Conditions Assessment) shall be conducted in accordance with the OSHPD approved methodology. OSHPD shall conduct review and approval of the Conditions Assessment.

Prior to performance of Conditions Assessment, permits shall be obtained from OSHPD. These projects may be processed in accordance with the FREER Manual as a Field Review project when the following information is provided:

- A copy of previously approved materials testing and assessment criteria.

- Construction documents which shall include at a minimum:

a.	An overall building floor plan showing the proposed locations of inspection, and;

b.	Emergency procedures for construction workers, and;

c.	Details and requirements for restoration of finishes and/or fire rated assemblies, and;

d.	When inspection impacts means of egress, a temporary exiting plan, and;

e.	Plans and details for temporary construction barriers, and;

f.	Fire watch procedures1.

During the Conditions Assessment, fire-resistive assemblies, fire-resistive construction and the means of egress shall be maintained in accordance with Chapters 7 and 33 of the California Fire Code. These plans and procedures shall be reviewed and approved by the OSHPD field staff (Area Compliance Officer, Fire and Life Safety Officer and District Structural Engineer) and the local fire authority (as applicable) in accordance with Section 3301 of the California Fire Code. Compliance with the provisions of Chapter 33 of the California Fire Code are in addition to any additional regulations or requirements pertaining to dust control, noise control and asbestos abatement enforced by agencies other than OSHPD FDD.

1When it is not possible to maintain fire-resistive assemblies, fire-resistive construction and/or the means of egress, temporary construction barriers and/or a fire watch shall be provided in accordance with OSHPD FDD CAN 9-3301 and OSHPD FDD PIN 14.

When demolition, inspection and reconstruction is continuous, no hot work is involved and inspectors and construction workers are in constant attendance, enforcement of temporary construction barrier and / or fire watch requirements may be deferred.  Under these conditions, appropriate procedures shall be established in the event of a fire or other emergency.