## A-Project Info
Testing, Inspection, and Observation Program
2019 California Building Standards Code OSHPD 2/5
This program is prepared and submitted for an OSHPD 2 or OSHPD 5 project. OSHPD 2 projects are limited to construction and remodel projects for: skilled nursing facilities and/or intermediate-care facilities of Type V, wood or light steel-frame construction (2019 CBC 1225.1). OSHPD 5 projects are limited to construction and remodel projects for: acute psychiatric hospitals subject to licensure (2019 CBC 1228.1).
SECTION A |  | PROJECT INFORMATION
Facility #: | Facility Name: |  | Project #:
Street Address:
City: |  | County:
Record Name (Scope of Project):
Abbreviations:
CAC: California Administrative Code |  | AAMA: American Architectural Manufacturers Association
CBC: California Building Code |  | NFPA: National Fire Protection Association
CEC: California Electrical Code |  | FM: FM Approval Standards
CMC: California Mechanical Code |  | DPOR: Design Professional of Record
CPC: California Plumbing Code
Testing, Inspection, and Observation Stages
Stage No. | Stage Name | Stage Scope / Description
1
DESIGN PROFESSIONAL OF RECORD RESPONSIBILITY
The administration of the work of construction, including this TIO, shall be under the responsible charge of an architect and structural engineer. When a structural engineer is not substantially involved, the architect shall be solely responsible. Where neither structural nor architectural elements are substantially involved, a mechanical or electrical engineer registered in the branch of engineering most applicable to the project may be in responsible charge. (CAC 7-141(a))
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
The "TIO Program Approval" from HCAI field staff must be obtained and included with the notice of start of construction required by CAC Section 7-137(a)4) and 7-145(a)5.A)
Construction shall not commence until the health facility has obtained from HCAI "TIO Program Approval". (CAC Section 7-135(a)3)
Note on I12: Project Number – As assigned by HCAI
Note on G15: Record Name (Scope of Project) – Scope of the project, as shown on the Application for New Project
Note on D23: TIO Stage Description - Provides a name and description/scope for each stage of a TIO program. Select the number of stages for your project by using the list box to the right of the project stage description. If the TIO program will be administered in a single stage then select "1 Stage". The number of stages on Tabs A, B, C, and D will automatically update when the number of stages is selected in the list box.

## B-Tests
|  |  | SECTION B |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | TESTS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual | Compliance Verification by IOR (Initial/Date) | HCAI/FDD Use (Initial/Date)
x1 | STRUCTURAL TESTS
| x11 | Foundation
|  |  | B-F1 |  | Soil fill CBC 1705.6 Fill material acceptance test
|  |  | B-F2 |  | Soil fill CBC 1705.6 Compaction test
|  |  | B-F3 |  | Soil and rock anchors CBC 1811 Load test
|  |  | B-F4 |  | Deep foundation elements CBC 1810.3.3.1.2, 1810.3.1.5.1, 1810.3.3.1.5, 1810.3.3.2, & 1810.3.10.4 Load test
|  |  | B-F5 |  | Shoring CBC 1812 Tie-Back Anchors
|  |  | B-F6 |  | Vibro Stone Columns (VSC) CBC 1813 Acceptance Test
|  |  | B-F7 |  | Investigations required (OSHPD 5 only) CBC 1803.2 Geotechnical investigation
B-F8
| x12 | Concrete
|  |  | B-C1 |  | Concrete CBC 1705.3, 1903.6 & 1910.1; ACI-318 1.9.1 & 26.4 Cementitious materials
|  |  | B-C2 |  | Concrete CBC 1705.3, 1903.5; ACI-318 1.9.1 & 26.4 Aggregates/Reactive aggregates
|  |  | B-C3 |  | Concrete CBC 1705.3, ACI-318 26.4.1.3, ASTM C1602 Water
|  |  | B-C4 |  | Concrete CBC 1705.3 & 1909.3.7; ACI-318 26.12.2.1(a) Strength test
|  |  | B-C5 |  | Concrete CBC 1705.3 & 1910.2 & ACI-318 20.2, 25.4.5.1 & 26.6.1.2 Metal reinforcement (including welded wire fabric and headed rebar)
|  |  | B-C6 |  | Concrete CBC 1705.3, 1901.3 & ACI-318 20.5 Headed studs and headed stud assemblies
|  |  | B-C7 |  | Concrete CBC Table 1705.3, 1903.8 Weldability of reinforcing bars
|  |  | B-C8 |  | Concrete CBC 1705.3 & 1910.3; ACI-318 20.3, 25.8 & 26.10.2 Prestressing tendons and anchorage
|  |  | B-C9 |  | Concrete CBC 1911.2; ACI-503.7 Crack repair by epoxy injection
|  |  | B-C10 |  | Concrete CBC 1911.3; ICC-ES AC 178 Sec. 9 Strengthening by externally bonded FRP
|  |  | B-C11 |  | Shotcrete CBC 1908.5 Preconstruction test
|  |  | B-C12 |  | Shotcrete CBC 1908.10 Strength test
|  |  | B-C13 |  | Shotcrete CBC 1705.19.1 Core test
|  |  | B-C14 |  | Post-installed anchors CBC 1901.3.4 Installation verification test (includes adhesive, shot pins and mechanical anchors)
|  |  | B-C15 |  | Existing post-installed anchors CBC 1708 and CAC Chapter 6, Section 11.3 Direct tension test
B-C16
B-C17
| x13 | Masonry
|  |  | B-MA1 |  | Masonry CBC 2105.2; TMS 602 1.4.B.3 Material standards tests
|  |  | B-MA2 |  | Masonry CBC 2105.3 Mortar test
|  |  | B-MA3 |  | Masonry CBC 2105.3 Grout test
|  |  | B-MA4 |  | Masonry CBC 2105.2; TMS 602 1.4.B.3 Compressive strength f'm - prism test
|  |  | B-MA5 |  | Masonry CBC 2105.4 Core test
|  |  | B-MA6 |  | Masonry CBC 1705.4 Masonry anchors
|  |  | B-MA7 |  | Veneer CBC 1410.2 Veneer bond strength test
|  |  | B-MA8 |  | Architectural Cast Stone CBC 2103.1, ASTM C1364 & TMS 504 Strength of stone anchorage
B-MA9
B-MA10
| x14 | Steel
|  |  | B-S1 |  | Steel CBC 2202.1 & AISC-360 Identification test for structural steel and cold formed steel
|  |  | B-S2 |  | Steel CBC 2213.1 & 1705.13.1 High strength bolts, nuts, and washers
|  |  | B-S3 |  | Steel CBC 2213.2 & 1705.13.1 End-welded studs
|  |  | B-S4 |  | Steel CBC 1705.2 & 1705.13.1.2 & AISC-360 & AISC-341 Nondestructive testing of welds
|  |  | B-S5 |  | Steel 1705.13.1.2 & AISC-341 K3 Buckling restrained brace load test
|  |  | B-S6 |  | Steel 2205.4, 1705.12.1 & AISC-341 K2 Beam to Column Moment Connections
B-S7
B-S8
| x15 | Other Structural Materials
|  |  | B-OM1 |  | Aluminum CBC 2003.1 Testing and Inspection
|  |  | B-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 AAMA 501.4 & 501.6 tests - Exterior glass curtain walls
|  |  | B-OM3 |  | Structural Sealant Glazing CBC 2410.1.2 Structural sealant tests - Exterior glass curtain walls
B-OM4
| x16 | Alternative Systems
|  |  | B-AS1 |  | Seismic Isolation System CBC 1705.13.4 Prototype and production test
|  |  | B-AS2 |  | Seismic Damping System CBC 1705.13.4 Prototype and production test
|  |  | B-AS3 |  | Structural Design Criteria CBC 104.11 Tests to support alternative system
B-AS4
B-AS5
B-AS6
| x17 | Nonstructural Components, Supports and Attachments
|  |  | B-N1 |  | Nonstructural Components CBC 1705.13.2
|  |  | B-N2 |  | Special Seismic Certification CBC 1705.13.3 Shake Table test
B-N3
B-N4
x2 | ELECTRICAL TESTS
|  |  | B-E1 |  | Ground Fault Protection of Equipment CEC 230.95(C) & 517.17(D)
|  |  | B-E2 |  | Emergency Generator Tests CEC 700.3(A) & NFPA 110-2016 § 7.13
|  |  | B-E3 |  | Automatic Transfer Switch Test NFPA 110-2016 § 7.13.4.1
|  |  | B-E4 |  | Emergency Stored Electrical Energy System Test NFPA 111-2016 Section 7.6
|  |  | B-E5 |  | Fire Pump Coordination Study and Testing CEC 695.3(C)(3)
|  |  | B-E6 |  | Essential Electrical System Coordination Study CEC 517.31(G) & 700.32
|  |  | B-E7 |  | Elevator Selective Coordination Study CEC 620.62
|  |  | B-E8 |  | Grounding System in Patient Care Spaces 2018 NFPA 99 6.3.3.1
|  |  | B-E9 |  | Hospital Grade Receptacles 2018 NFPA 99 6.3.3.2.5
|  |  | B-E10 |  | Isolated Power Systems – Line Isolation Monitor Test 2018 NFPA 99 6.3.3.3.2
|  |  | B-E11 |  | Isolated Power Systems – Impedance of Isolated Wiring Test 2018 NFPA 99 6.3.2.9.2.1
|  |  | B-E12 |  | Medium Voltage Outdoor Systems – Inspections and Test CEC 225.56
|  |  | B-E13 |  | Medium Voltage Cable Testing CEC 328.14 & ANSI/NECA/NCSCB 600-2014
|  |  | B-E14 |  | Insulation Testing CEC 110.7, 2018 NFPA 99 6.7.4.1.2.2
|  |  | B-E15 |  | Torque Electrical Connections CEC 110.3(B) & 110.14(D)
|  |  | B-E16 |  | Temporary Installation Grounding CEC 590.6
|  |  | B-E17 |  | Nurse call system CEC 517.123
|  |  | B-E18 |  | Arc Energy Reduction CEC 240.67 & 240.87
|  |  | B-E19 |  | Short-Circuit Current Calculations CEC 110.24(A), 409.22, 430.99, 440.10(B)
|  |  | B-E20 |  | Available Fault and Short-Circuit Current Field Marking CEC 110.16(B), 110.24(A), 620.51(D)(1), 700.5(E)
|  |  | B-E21 |  | Means of Egress Illumination CBC 1008.2 and 1008.3 Illumination and Emergency Power
|  |  | B-E22 |  | Lighting (OSHPD 5) CBC 1228.4.21 Tamper Resistant
B-E23
x3 | MECHANICAL TESTS
|  |  | B-ME1 |  | Listed hood assemblies CMC 508.2
|  |  | B-ME2 |  | Commercial kitchen hood ventilation CMC 511.2.2.1 Performance test
|  |  | B-ME3 |  | Refrigeration equipment CMC 1116.0
|  |  | B-ME4 |  | Refrigeration detection and alarm system CMC 1108.4 & CFC 605.6 Acceptance testing
|  |  | B-ME5 |  | Refrigeration flaring system CMC 1114.3 Safety and effectiveness
|  |  | B-ME6 |  | Steam and hot water boilers CMC 1013.0
|  |  | B-ME7 |  | Hydronics CMC 1205.2, 1220.2.6 & 1221.3 Pressure test of steam and water piping
|  |  | B-ME8 |  | Process piping CMC 1405.2.2 Pressure test
|  |  | B-ME9 |  | Pre Demolition Air Balance CMC 407.3.1 Pre-demolition Air Balance Test and Report
|  |  | B-ME10 |  | Post Demolition Air Balance CMC 407.3.1 Air Balance Test and Report
|  |  | B-ME11 |  | Ventilation system Air Balance CMC 407.3.1 & Table 4-A Areas tested and balanced
|  |  | B-ME12 |  | Duct Leakage Test CMC 603.10.1 SMACNA HVAC Air Duct Leakage Test
|  |  | B-ME13 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 416.4 Alarm system test
|  |  | B-ME14 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 417.0 Mechanical system tested and balanced
B-ME15
B-ME16
x4 | PLUMBING TESTS
|  |  | B-P1 |  | Disinfection of potable water systems CPC 609.9
|  |  | B-P2 |  | Medical gas and vacuum NFPA 99-2018 § 5.1.12 Gas and vacuum system performance testing
|  |  | B-P3 |  | Medical gas and vacuum NFPA 99-2018 § 5.1.12 Gas and vacuum system verifcation testing
|  |  | B-P4 |  | Existing sewers and drains CPC 102.4.1, 105.3, 105.3.2, & 712.0 Tested for conformance with requirements for new work
|  |  | B-P5 |  | Water supply system CPC 105.3, 105.3.2, & 609.4 Pressure tested prior to covering or concealment
|  |  | B-P6 |  | Plumbing, drainage, and venting systems CPC 105.3, 105.3.2, & 712.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P7 |  | Building sewer CPC 105.3, 105.3.2, 712.0 & 723.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P8 |  | Storm drain piping CPC 1107.1 Water or air tested prior to use, covering or concealment
|  |  | B-P9 |  | Fuel piping CPC 1213.0 Air, CO2 or nitrogen tested prior to use, covering or concealment
|  |  | B-P10 |  | Private sewer disposal system CPC 105.0, 105.3.2, & CPC Appendix H H1001.2 Tested prior to use, covering or concealment
|  |  | B-P11 |  | Protectively coated pipe CPC 312.5 Tested for voids, damage and imperfections
|  |  | B-P12 |  | Defective systems CPC 105.3.1, 105.3.2, 712.0 Air test of defective drainage and plumbing systems
|  |  | B-P13 |  | Shower receptors CPC 408.7.5
|  |  | B-P14 |  | Backflow prevention devices and assemblies CPC 603.2 & 603.4.2 Assembly tested
|  |  | B-P15 |  | Nonpotable water CPC 1502.0 Testing of alternate water sources and cross-connections
|  |  | B-P16 |  | Recycled water supply systems CPC 1505.5 & 1505.13 Initial cross-connection test and system testing before initial operation
|  |  | B-P17 |  | On-site treated nonpotable gray water systems CPC 1506.5, 1506.12, 1502.1 Initial cross-connection test and system testing before initial operation
|  |  | B-P18 |  | Handwashing Stations (OSHPD 5) CBC 1228.4.22 Ligature-resistant features
B-P19
x5 | FIRE PROTECTION AND LIFE SAFETY SYSTEMS
|  |  | B-FP1 |  | Fire Alarm CFC 901.5 & CFC 907.7 NFPA 72-2016 §14.4 Acceptance and Reacceptance Testing
|  |  | B-FP2 |  | Fire and smoke dampers CFC 901.5 & CFC 907.8 Acceptance testing
|  |  | B-FP3 |  | Duct Detectors CFC 901.5, NFPA 72-2016 §14.4 Differential Pressure Test
|  |  | B-FP4 |  | Smoke control system CFC 901.5, CFC 909.18 & CBC 1705.18 Acceptance testing
|  |  | B-FP5 |  | Fire sprinkler CFC 901.5 & NFPA 13-2016 Chapter 25 Acceptance testing – Aboveground piping
|  |  | B-FP6 |  | Fire sprinkler CFC 901.5 & NFPA 13-2016 Chapter 25 Acceptance testing – Underground piping
|  |  | B-FP7 |  | Standpipe system CFC 901.5 & NFPA 14-2016 Chapter 11 Acceptance testing – Aboveground piping
|  |  | B-FP8 |  | Standpipe system CFC 901.5, CFC 905.3.1 & NFPA 14-2016 Chapter 11 Acceptance testing in buildings 4-stories or more
|  |  | B-FP9 |  | Standpipe system CFC 901.5 & NFPA 14-2016 Chapter 11 Acceptance testing – Underground piping
|  |  | B-FP10 |  | Private fire mains CFC 901.5 & NFPA 24-2016 § 10.10 Acceptance testing
|  |  | B-FP11 |  | Fire pumps CFC 901.5 & NFPA 20-2016 § 14.1 & 14.2 Acceptance testing
|  |  | B-FP12 |  | Fire protection water tank CFC 901.5 & NFPA 22-2018 Chapter 17 Acceptance testing
|  |  | B-FP13 |  | Wet chemical extinguishing system CFC 901.5 & NFPA 17A-2017 § 6.4 Acceptance testing
|  |  | B-FP14 |  | Clean agent extinguishing system CFC 901.5 & NFPA 2001-2015 § 7.7 Acceptance testing
|  |  | B-FP15 |  | CO2 extinguishing system CFC 901.5 & NFPA 12-2015 § 4.4.3 & 4.4.4 Acceptance testing
|  |  | B-FP16 |  | Dry chemical extinguishing system CFC 901.5 & NFPA 17-2017 § 10.4 Acceptance testing
|  |  | B-FP17 |  | Halon 1301 extinguishing system CFC 901.5 & NFPA 12A-2015 § 6.7 Acceptance testing
|  |  | B-FP18 |  | Underground fuel storage tank CFC 5704.2.12 & NFPA 30-2018 § 21.5.1 Initial testing
|  |  | B-FP19 |  | Underground fuel storage tank CFC 5704.2.12 & NFPA 30-2018 § 21.5.2 Tightness testing
|  |  | B-FP20 |  | Flammable and combustible liquid fuel piping CFC 5703.6.3 Pressure testing
|  |  | B-FP21 |  | Emergency Responder Radio Coverage CFC 510.5.3 Acceptance test procedure
|  |  | B-FP22 |  | Testing of Elevator Shutdown CBC 3005.5, NFPA 72-2016 21.4 and ASME A17.1-2013
|  |  | B-FP23 |  | Elevator Emergency Operation CBC 3003.2 Emergency Recal and In-cart operation
|  |  | B-FP24 |  | Elevator Emergency Standby Power CBC 3003.1 Backup Generator Engaged
B-FP25
B-FP26
x6 | OTHER TESTS
|  |  | B-OT1 |  | Radiation Shielding Barriers CBC 1705.1.1 and 3102C Radiation shielding barrier test
|  |  | B-OT2 |  | Doors and Door Openings (OSHPD 5) CBC 1228.4.8 Keyed locks, hinges and door levers
|  |  | B-OT3 |  | Windows and Screens (OSHPD 5) CBC 1228.4.9 Glazing, openings, impact loads, operable windows
|  |  | B-OT4 |  | Ceilings (OSHPD 5) CBC 1228.4.11.1 All M, E, P shall be concealed
|  |  | B-OT5 |  | Grab Bars (OSHPD 5) CBC 1228.4.18 Anchorage, graspability, and ligature resistant
|  |  | B-OT6 |  | Built-In-Furnishings (OSHPD 5) CBC 1228.4.20 In areas accessible to patients
|  |  | B-OT7 |  | Outdoor Activity Area (OSHPD 5) CBC 1228.13.12 Fences doors, gates, lights, cameras and furniture
|  |  | B-OT8 |  | Handwashing Stations (OSHPD 5) CBC 1228.4.22 Ligature-resistant, laminar flow, goose neck spouts
Note on D3: Project information in this row is referenced from Tab A-Project Info
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on F5: Blank rows are provided to add any additional tests which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F55: Required for projects that use aluminum as a structural material.
Note on F56: Required for projects that include glazing scope that uses structrual sealant.
Note on F60: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F61: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F62: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F67: In the absence of calculations or experience data, testing may be required.
Note on F68: Required on projects where equipment requiring special seismic certification has not been preapproved or justified by analysis.
Note on F72: For 480V electrical "service" rated 1000A or more, and a feeder meeting CEC 215.10. (NOT FOR GFCI TESTING).
Note on F75: Testing of UPS and other battery storage systems used as energy storage system. Note: An UPS supplied by an emergency power supply system (EPSS) like an essential electrical system is not required to be tested to NFPA 111.
Note on F76: Not required for most fire pump installations. Only for new fire pumps in multi-building campus style complexes. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F77: Study required from the Electrical Engineer of Record (EEOR) when new circuit breakers and fuses are installed in new and existing essential electrical systems. Single line diagram and over current protective devices in study shall match approved electrical plans. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F78: Applies to elevator, elevators, dumbwaiters, escalators, moving walks, platform lifts, and stairway chairlifts installations. Study required from the Electrical Engineer of Record (EEOR) when more than one machine is fed from one feeder. Single line diagram and over current protective devices in study shall match approved electrical plans. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F79: Voltage and impedance measurements when new electrical circuits and receptacles are installed in patient care spaces like head walls.
Note on F80: Receptacle retention force test when new receptacles are installed in patient care spaces like head walls.
Note on F82: Related to Isolated Power System - Line Isolation monitor test.
Note on F83: Medium voltage (over 1000v) may be used for a large hospital campus. Pre-energization and operational tests for new and modified electrical systems over 1000V.
Note on F84: Testing of new medium volt cables (1kv - 100kv). Related to Medium Voltage Outdoor Systems – Inspections and Test.
Note on F85: Megger test of new conductors to ensure wiring is free from short circuits and ground faults.
Note on F86: For panelboards, switchboards, switchgear, MCC, and other electrical equipment that require electrical connections to be torqued per manufacture instructions.
Note on F87: For temporary work.
Note on F88: For new or modified nurse call systems. This is a functional test.
Note on F89: For 1200amp or larger electrical equipment installations.
Note on F90: Required for new panelboards, switchboards, switchgear, MCC, ATS, and elevator controllers. Study from the Electrical Engineer of Record (EEOR) for stating all new electrical equipment SCCR/AIC ratings meet or exceed available fault currents values determined in the study. Study used in the field to verify installed equipment SCCR/AIC match the information provided in the study.
Note on F91: Labeling required for new electrical "service" equipment (i.e. main switchboard).
Note on F93: Lighting in areas identified in the Patient Safety Risk Assessment as high- and medium-risk areas
Note on F96: Listed hood assemblies shall be tested per manufacturers. Listed UV hoods tested IAW UL 710 and 710C.
Note on F97: Performance test before final approval of install of ventilation system.
Note on F98: Factory and field refrigeration system pressure testing.
Note on F99: Alarm system testing of machinery room alarm systems.
Note on F100: Report for approved agency detailing emission products.
Note on F101: Inspection and test protocol for boilers after installation and prior to use.
Note on F102: Pressure testing for system piping and components. Note: piping to be installed in concrete shall be tested per these requirements prior to pouring concrete.
Note on F103: Pressure test at completion of installation.
Note on F104: Survey of exisitng ventilation system priory to start of remodel work.
Note on F105: Survey of ventilation system at completion of remodel work to ensure pre-demolition air balance values are maintained.
Note on F106: Test and balance of new spaces, spaces affected by new equipment or spaces with change in function after completion of work.
Note on F108: Testing of air pressure alarm systems prior to acceptance.
Note on F109: Test and balance of mechanical system after completion of work.
Note on F115: Testing to be done for new piping and when pipes have been breached in project. Not for fixture replacement.
Note on F116: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F117: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F118: Testing for modified or breached sewer piping.
Note on F119: Testing of completion of new segment or entire system.
Note on F122: Water or air testing for new storm drain piping, and parts of existing storm drain piping that have been altered, extended, or repaired.
Note on F123: Testing required for new, or repaired fuel piping prior to acceptance and initial operation.
Note on F124: Static and fluid water testing after installation.
Note on F126: Air testing of existing drainage or plumbing that is suspected to be defective.
Note on F127: Standing water test for drain/receptor interface.
Note on F128: Device shall be approved by the AHJ and then tested at time of installation, repair, or relocation.
Note on F129: Testing of all new alternate water sources for nonpotable water including testing emphasis on cross-connection prevention.
Note on F130: Handwashing fixtures that are accessible to patients, including those located in patient rooms and patient toilet rooms
Note on F133: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F134: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F135: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independetly. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F136: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independetly. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F137: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independetly. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F138: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F139: For new installations, remodels, replacements or repairs. If components that affect performance are replaced, then a retest shall be conducted by the pump manufacturer or designated representative or qualified persons acceptable to HCAI.
Note on F140: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test. Prior to placing the tank in service, a representative of the tank contractor and a representative of the owner shall conduct a joint inspection of the completed equipment.
Note on F141: For new installations, remodels, replacements or repairs.
Note on F142: For new installations, remodels, replacements or repairs.
Note on F143: For new installations, remodels, replacements or repairs.
Note on F144: For new installations, remodels, replacements or repairs.
Note on F145: For new installations, remodels, replacements or repairs.
Note on F146: For new installations, remodels, replacements or repairs.
Note on F147: For new installations, remodels, replacements or repairs.
Note on F148: For new installations, remodels, replacements or repairs.
Note on F149: For new installations, remodels, replacements or repairs.
Note on F150: For new installations, remodels, replacements or repairs.
Note on F151: For new installations, remodels, replacements or repairs.
Note on F152: For new installations, remodels, replacements or repairs.
Note on F155: Required on all projects that contain imaging equipment radiation shielding barriers.
Note on F161: When indicated by the patient Safety Risk Assesment
Note on F162: Windows in patient care areas or areas used by patients
Note on F163: Ceilings shall be monolithic in seclusion rooms, exam/treatment rooms, patient bedrooms, patient toilet rooms, or patient bathing facilities
Note on F164: Grab bars, including those that are part of fixtures such as soap dishes, shall be sufficiently anchored to sustain a concentrated load of 250 pounds (113.4 kg)
Note on F165: Specific requirements for shelves, clothing rods and hooks. Not permited: doors and drawers, towel bars, shower curtain rods, levers and handles
Note on F166: Specifc requirements for fence, gate and door design and intallation, lighting, security cameras, and furniture
Note on F167: Handwashing sinks accessible to patients

## C-On-Site Special Inspections
|  |  | SECTION C |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | ON-SITE SPECIAL INSPECTIONS | Samples of test & inspection reports included | OPAA No. and Expiration Date | RESPONSIBLE APPROVED AGENCY AND/OR INDIVIDUAL (IDENTIFY SPECIAL INSPECTOR) | COMPLIANCE VERIFICATION BY IOR (Initial/Date) | HCAI/FDD USE (Initial/Date)
x1 | STRUCTURAL SPECIAL INSPECTIONS
| x11 | Foundation
|  |  | C-F1 |  | Soils CBC 1705.6 Soil fill
|  |  | C-F2 |  | Foundation CBC 1705.7 Driven deep foundations
|  |  | C-F3 |  | Foundation CBC 1705.8 Cast-in-place deep foundations
|  |  | C-F4 |  | Foundation CBC 1705.9 Helical pile foundations
|  |  | C-F5 |  | Shoring CBC 1812 Shoring
|  |  | C-F6 |  | Vibro Stone Columns (VSC) CBC 1813 Vibro Stone Columns
|  |  | C-F7 |  | Prestressed soil and rock anchors CBC 1705.3, 1811 & 1812 Installation and testing
C-F8
C-F9
| x12 | Concrete
|  |  | C-C1 |  | Concrete CBC 1705.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | C-C2 |  | Concrete CBC 1705.3; ACI-318 26.4.1.5 Admixtures
|  |  | C-C3 |  | Concrete CBC 1705.3; ACI-318 26.4 Mix Design
|  |  | C-C4 |  | Concrete CBC 1705.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | C-C5 |  | Concrete CBC 1705.3 CIP & Post-installed anchors
|  |  | C-C6 |  | Concrete CBC Table 1705.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | C-C7 |  | Concrete CBC 1705.3; ACI-318 26.13 Specialty inserts, Stud rails, Rebar mechanical conn., Headed rebar
|  |  | C-C8 |  | Concrete CBC 1705.3.3 Batch plant inspection
|  |  | C-C9 |  | Concrete CBC 1705.3.4; ACI-318 26.13 Prestressed concrete
|  |  | C-C10 |  | Concrete CBC 1705.3 & 1705.12.5 Precast concrete erection
|  |  | C-C11 |  | Shotcrete CBC 1705A.19 & 1908A Installation
|  |  | C-C12 |  | Concrete CBC 1705.3 Insulating concrete
|  |  | C-C13 |  | Concrete CBC 1705.3, 1705.3.1, 1903.8 Welding of reinforcing bars
|  |  | C-C14 |  | Concrete CBC 1705.12.5 GFRC panels
|  |  | C-C15 |  | Concrete CBC 1911.2; ACI-503.7 Crack repair by epoxy injection
|  |  | C-C16 |  | Concrete CBC 1911.3, ICC AC178 Sec. 3 to 8 Strengthening by externally bonded FRP
C-C17
C-C18
C-C19
| x13 | Masonry
|  |  | C-MA1 |  | Masonry CBC 1705.4 Laying and grouting
|  |  | C-MA2 |  | Masonry CBC 2104A.1.3 Low lift grout
|  |  | C-MA3 |  | Masonry CBC 2104A.1.3 High lift grout
|  |  | C-MA4 |  | Masonry CBC 1705.4 Masonry anchors
C-MA5
C-MA6
| x14 | Steel
|  |  | C-S1 |  | Steel CBC 1705.2.5 & 1705.12.1 Automatic end-welded studs
|  |  | C-S2 |  | Steel CBC 1705.2.5 & 1705.12.1 Shop and field welding
|  |  | C-S3 |  | Steel AWS D1.1 3 & 4 and AWS D1.8 6.1 Shop and field welding - WPS / WPQR
|  |  | C-S4 |  | Steel CBC 1705.2 & 1705.12.1 High strength bolt installation
|  |  | C-S5 |  | Steel CBC 1705.2, 1705.11.2 & 1705.12.3 Cold-formed steel light frame construction
C-S6
C-S7
C-S8
| x15 | Wood
|  |  | C-W1 |  | Wood CBC 1705.5, 1705.5.4, 1705.11.1 & 1705.12.2 Glue laminated timber
|  |  | C-W2 |  | Wood CBC 1705.5.6, 1705.11.1 & 1705.12.2 Installation of timber connectors
|  |  | C-W3 |  | Wood CBC 1705.5, 1705.5.2 & 1705.5.5 Manufactured trusses
|  |  | C-W4 |  | Wood CBC 1705.11.1 & 1705.12.2 Nailing, screw attachment, bolting, anchoring, field gluing operations and other fastening
C-W5
C-W6
| x16 | Other Structural Materials
|  |  | C-OM1 |  | Aluminum CBC 2003.1 Testing and Inspection
|  |  | C-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 Structural sealants for exterior glass curtain walls
C-OM3
C-OM4
| x17 | Alternative Systems
|  |  | C-AS1 |  | Alternative system CBC 1705.1.1 Construction materials and methods for alternative system
|  |  | C-AS2 |  | Seismic Isolation System CBC 1705.12.8 Fabrication, installation, prototype, and production testing
|  |  | C-AS3 |  | Seismic Damping System CBC 1705.12.8 Fabrication, installation, prototype, and production testing
C-AS4
| x18 | Nonstructural components, supports and attachments
|  |  | C-N1 |  | Architectural components CBC 1705.12.5 & 1705.16 Cladding, nonbearing walls and veneer
|  |  | C-N2 |  | Ceiling CBC 1705.12.5 Suspended ceiling systems and their anchorage
|  |  | C-N3 |  | Access floors CBC 1705.12.5.1 Anchorage of access floor systems
|  |  | C-N4 |  | Storage racks 8’ or taller CBC 1705.12.7 Anchorage
|  |  | C-N5 |  | Plumbing, mechanical and electrical components CBC 1705.12.6 Anchorage, bracing, and vibration isolators
|  |  | C-N6 |  | Special Seismic Certification CBC 1705.12.4 Special Seismic Certification label, anchorage and mounting
C-N7
C-N8
x2 | ELECTRICAL INSPECTIONS
|  |  | C-E1 |  | Available Fault and Short-Circuit Current Field Marking CEC 110.16(B), 110.24(A), 620.51(D)(1), 700.5(E)
C-E2
C-E3
x3 | MECHANICAL INSPECTIONS
C-M1
C-M2
x4 | PLUMBING INSPECTIONS
C-P1
C-P2
x5 | FIRE PROTECTION AND LIFE SAFETY SYSTEM SPECIAL INSPECTIONS
|  |  | C-FP1 |  | Sprayed fire-resistant materials CBC 1705.14 Spray-applied fireproofing
|  |  | C-FP2 |  | Mastic and intumescent fire-resistant coatings CBC 1705.15 In accordance with AWCI 12-B
|  |  | C-FP3 |  | Penetration firestops CBC 1705.17.1 Penetration firestop systems that are tested and listed
|  |  | C-FP4 |  | Fire-resistant joint systems CBC 1705.17.2 Fire-resistant joint systems that are tested and listed
|  |  | C-FP5 |  | Smoke control systems CFC 909.18.8 & CBC 170.17 & 1705.18 Ductwork and operation
|  |  | C-FP6 |  | Sprinkler system piping NFPA 13-2016 § 6.5.2 Welded pipe and fittings
|  |  | C-FP7 |  | Standpipe system piping NFPA 14-2016 § 4.4.2 Welded pipe and fittings
C-FP8
C-FP9
x6 | OTHER SPECIAL INSPECTIONS
|  |  | C-OT1 |  | Exterior insulation and finish systems (EIFS). CBC 1705.16 EIFS applications
|  |  | C-OT2 |  | Water-resistive barrier coating CBC 1705.16.1 & ASTM E2570 Barrier coating when installed over a sheathing substrate.
|  |  | C-OT3 |  | Substrate for Roof Coverings CBC 1507 Requirements for Roof Coverings
|  |  | C-OT4 |  | Installation of Roof Coverings CBC 1506 Materials
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F75: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F76: Required on projects with equipment requiring special seismic certification.
Note on F90: For new, remodel, or replacement projects. This type of test is applied to floor, roof, and wall assemblies, and structural members. Consider OPD-0091-13 for Fire-Resistive Standard Details.
Note on F91: Applicable for structural elements on new, remodel, or replacement projects.
Note on F92: For new, remodel, or replacement projects.
Note on F93: For new, remodel, or replacement projects.
Note on F94: For new, remodel, or replacement projects when having erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location. Also prior to occupancy and after sufficient completion for the purposes of pressure-difference testing, flow measurements, and detection and control verification.
Note on F95: For new, remodel, or replacement projects when there is welding sprinkler pipe.
Note on F96: For new, remodel, or replacement projects when standpipe system piping is welded.

## D-Off-Site Special Inspections
|  |  | SECTION D |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | OFF-SITE SPECIAL INSPECTIONS | Samples of test & inspection reports included | OPAA No. and Expiration Date | RESPONSIBLE APPROVED AGENCY AND/OR INDIVIDUAL (IDENTIFY SPECIAL INSPECTOR) | COMPLIANCE VERIFICATION BY IOR (Initial/Date) | HCAI/FDD USE (Initial/Date)
x1 | STRUCTURAL SPECIAL INSPECTIONS
| x11 | Concrete
|  |  | D-C1 |  | Concrete CBC 1705.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | D-C2 |  | Concrete CBC 1705.3; ACI-318 26.4.1.5 Admixtures
|  |  | D-C3 |  | Concrete CBC 1705.3; ACI-318 26.4 Mix Design
|  |  | D-C4 |  | Concrete CBC 1705.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | D-C5 |  | Concrete CBC 1705.3 CIP & Post-installed anchors
|  |  | D-C6 |  | Concrete CBC Table 1705.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | D-C7 |  | Concrete CBC 1705.3; ACI-318 26.13 Specialty inserts, Stud rails, Rebar mechanical conn., Headed rebar
|  |  | D-C8 |  | Concrete CBC 1705.3.3 Batch plant inspection
|  |  | D-C9 |  | Concrete CBC 1705.3.4; ACI-318 26.13 Prestressed concrete
|  |  | D-C10 |  | Concrete CBC 1705.3 Precast concrete fabrication & precast panels
|  |  | D-C11 |  | Concrete CBC 1705.3 Insulating concrete
|  |  | D-C12 |  | Concrete CBC 1705.3, 1705.3.1, 1903.8 Welding of reinforcing bars
|  |  | D-C13 |  | Concrete CBC 1705.12.5 GFRC panels
|  |  | D-C14 |  | Concrete CBC 1911.3, ICC AC178 Sec. 3 to 8 Strengthening by externally bonded FRP
D-C15
D-C16
| x12 | Masonry
|  |  | D-MA1 |  | Masonry CBC 1705.4 Masonry anchors
D-MA2
D-MA3
| x13 | Steel
|  |  | D-S1 |  | Steel CBC 1705.2 & 1705.12.1, AISC-360 & AISC-341 Steel shop fabrication
|  |  | D-S2 |  | Steel CBC 1705.2.5 & 1705.12.1 Automatic end-welded studs
|  |  | D-S3 |  | Steel CBC 1705.2.5 & 1705.12.1 Shop welding
|  |  | D-S4 |  | Steel AWS D1.1 3 & 4 and AWS D1.8 6.1 Shop welding - WPS / WPQR
|  |  | D-S5 |  | Steel CBC 1705.2 & 1705.12.1 High strength bolt installation
|  |  | D-S6 |  | Steel CBC 1705.2, 1705.11.2 & 1705.12.3 Cold-formed steel light frame construction
D-S7
D-S8
| x14 | Wood
|  |  | D-W1 |  | Wood CBC 1705.5, 1705.5.4, 1705.11.1 & 1705.12.2 Glue laminated timber
|  |  | D-W2 |  | Wood CBC 1705.5.6, 1705.11.1 & 1705.12.2 Installation of timber connectors
|  |  | D-W3 |  | Wood CBC 1705.5, 1705.5.2 & 1705.5.5 Manufactured trusses
|  |  | D-W4 |  | Wood CBC 1705.11.1 & 1705.12.2 Nailing, screw attachment, bolting, anchoring, field gluing operations and other fastening
D-W5
D-W6
| x15 | Other Structural Materials
|  |  | D-OM1 |  | Aluminum CBC 2003.1 Inspection
|  |  | D-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 Structural sealants for exterior glass curtain walls
D-OM3
| x16 | Alternative Systems
|  |  | D-AS1 |  | Alternative system CBC 1705.1.1 Construction materials and methods for alternative system
|  |  | D-AS2 |  | Seismic Isolation System CBC 1705.12.8 Fabrication, installation, prototype, and production testing
|  |  | D-AS3 |  | Seismic Damping System CBC 1705.12.8 Fabrication, installation, prototype, and production testing
D-AS4
| x17 | Nonstructural components, supports and attachments
|  |  | D-N1 |  | Architectural components CBC 1705.12.5 & 1705.16 Cladding, nonbearing walls and veneer
|  |  | D-N2 |  | Ceiling CBC 1705.12.5 Suspended ceiling systems and their anchorage
|  |  | D-N3 |  | Access floors CBC 1705.12.5.1 Anchorage of access floor systems
|  |  | D-N4 |  | Storage racks 8’ or taller CBC 1705.12.7 Anchorage
|  |  | D-N5 |  | Plumbing, mechanical and electrical components CBC 1705.12.6 Anchorage, bracing, and vibration isolators
|  |  | D-N6 |  | Special Seismic Certification CBC 1705.12.4 Special Seismic Certification label, anchorage and mounting
D-N7
D-N8
x2 | MECHANICAL INSPECTIONS
D-M1
D-M2
x3 | PLUMBING INSPECTIONS
D-P1
D-P2
x4 | FIRE PROTECTION AND LIFE SAFETY SYSTEMS SPECIAL INSPECTIONS
|  |  | D-FP1 |  | Sprayed fire-resistant materials CBC 1705.14 Spray-applied fireproofing
|  |  | D-FP2 |  | Mastic and intumescent fire-resistant coatings CBC 1705.15 In accordance with AWCI 12-B
|  |  | D-FP3 |  | Penetration firestops CBC 1705.17.1 Penetration firestop systems that are tested and listed
|  |  | D-FP4 |  | Fire-resistant joint systems CBC 1705.17.2 Fire-resistant joint systems that are tested and listed
|  |  | D-FP5 |  | Smoke control systems CFC 909.18.8 & CBC 170.17 & 1705.18 Ductwork and operation
|  |  | D-FP6 |  | Sprinkler system piping NFPA 13-2016 § 6.5.2 Welded pipe and fittings
|  |  | D-FP7 |  | Standpipe system piping NFPA 14-2016 § 4.4.2 Welded pipe and fittings
D-FP8
D-FP9
x5 | OTHER SPECIAL INSPECTIONS
|  |  | D-OT1 |  | Exterior insulation and finish systems (EIFS) CBC 1705.16 EIFS applications
|  |  | D-OT2 |  | Water-resistive barrier coating CBC 1705.16.1 & ASTM E2570 Barrier coating when installed over a sheathing substrate.
D-OT3
D-OT4
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F45: Required for projects that use aluminum as a structural material.
Note on F46: Required for projects that include glazing scope that uses structrual sealant.
Note on F49: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F50: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F51: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F58: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F59: Required on projects with equipment requiring special seismic certification.
Note on F69: For new, remodel, or replacement projects. This type of test is applied to floor, roof, and wall assemblies, and structural members. Consider OPD-0091-13 for Fire-Resistive Standard Details.
Note on F70: Applicable for structural elements on new, remodel, or replacement projects.
Note on F71: For new, remodel, or replacement projects.
Note on F72: For new, remodel, or replacement projects.
Note on F73: Applicable for new, remodel, replacement, repair projects when having erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location. Also prior to occupancy and after sufficient completion for the purposes of pressure-difference testing, flow measurements, and detection and control verification.
Note on F74: For new, remodel, or replacement projects when there is welding sprinkler pipe.
Note on F75: For new, remodel, or replacement projects when standpipe system piping is welded.

## E-Required Compliance Forms
|  |  | SECTION E |  |  | REQUIRED COMPLIANCE FORMS
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | FORM # | Required (Select with "X") | DOCUMENT NAME | RESPONSIBLE DESIGNER OR INSTALLING CONTRACTOR | COMPLIANCE VERIFICATION BY IOR (Initial/Date) | HCAI/FDD USE (Initial/Date)
x1 | CALIFORNIA ENERGY CODE
| x11 | NON-RESIDENTIAL CERTIFICATE OF INSTALLATION (NRCI)
|  |  | NRCI-ENV-01-E |  | ENVELOPE
|  |  | NRCI-MCH-01-E |  | MECHANICAL
|  |  | NRCI-PLB-01-E |  | PLUMBING
|  |  | NRCI-LTI-01-E |  | INDOOR LIGHTING (conditioned, processed spaces)
|  |  | NRCI-LTI-02-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTI-04-E |  | TWO INTERLOCKED LIGHTING SYSTEMS (conditioned, processed spaces)
|  |  | NRCI-LTI-05-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTI-06-E |  | VIDEO CONFERENCE STUDIO LIGHTING (conditioned, processed spaces)
|  |  | NRCI-LTI-01-E |  | INDOOR LIGHTING (conditioned, processed spaces)
|  |  | NRCI-LTI-02-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTI-05-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTO-01-E |  | OUTDOOR LIGHTING
|  |  | NRCI-LTO-02-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (outdoor lighting)
|  |  | NRCI-ELC-01-E |  | ELECTRICAL POWER DISTRIBUTION
|  |  | NRCI-PRC-01-E |  | COVERED PROCESSES (commercial refrigeration)
|  |  | NRCI-PRC-01-E |  | COVERED PROCESSES (parking garage)
|  |  | NRCI-PRC-01-E |  | COVERED PROCESSES (process boilers greater than 2.5 MM Btu/h)
|  |  | NRCI-LTS-01-E |  | SIGN LIGHTING (indoor and outdoor)
| x12 | NON-RESIDENTIAL CERTIFICATE OF ACCEPTANCE (NRCA)
|  |  | NRCA-ENV-02-F |  | FENESTRATION ACCEPTANCE
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional documentation required by local AHJs or other entities specific to the project
Note on G5: Name of the installing contractor which under their purview the items were installed and/or to meet the requirements documented in the NRCC, NRCA and approved construction documents
Note on I5: The IOR shall place their initials and date in this column to indicate they received all of the required documentation for the installation and/or testing for the item(s) required by the NRCI, NRCA and approved construction documents.

## F-Cons Verif
SECTION F |  |  | CONSTRUCTION VERIFICATION
Facility #: | Facility Name: | [7 empty] | Project #:
VERIFIED CONSTRUCTION INSPECTION AND OBSERVATION REPORTING | [11 empty] | HCAI/FDD USE
REFERENCE NUMBER |  | PROJECT STAGE(S), MILESTONE, OR INTERVAL (Clearly indicate which Stage(s) apply to which Milestone/Interval) | VERIFIED COMPLIANCE REPORT REQUIRED AS INDICATED (Form OSH-FD-123) (See “PERSONAL KNOWLEDGE” as defined in California Administrative Code, Section 7-151)
|  |  | GEOR | AOR | SEOR | MEOR | EEOR | CONT | IOR | SP INSP | TEST LAB
Clear all plan review Outstanding Items List (OIL) Items
Installation of temporary equipment
Removal of temporary equipment
Substantial Compliance (Remodel, Renovations, Maintenance projects, Equipment Replacement)
Certificate of Occupancy (New Buildings, Additions, Changes in Occupancy)
Construction Final
ABBREVIATIONS: |  | GEOR - Geotechnical Engineer of Record |  | AOR - Architect of Record |  |  |  |  | SEOR - Structural Engineer of Record
|  | MEOR - Mechanical Engineer of Record |  | EEOR - Electrical Engineer of Record |  |  |  |  | CONT O/B - Contractor or Owner/Builder
|  | SP. INSP - Special Inspector |  | IOR - Inspector of Record |  |  |  |  | Test Lab – Engr. For the approved agency
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on F5: Describe each project stage, milestone, or interval for which one or more Verified Compliance Report is required. per CAC 7-141(i) and 7-151(f). A milestone or interval can include multiple stages.
Note on G6: GEOR = Geotechnical Engineer of Record
Note on H6: AOR = Architect or Record (often the Architect in Responsible Charge of the entire project)
Note on I6: SEOR = Structural Engineer of Record
Note on J6: MEOR = Mechanical Engineer of Record
Note on K6: EEOR = Electrical Engineer of Record
Note on L6: CONT = Contractor
Note on M6: IOR = Inspector of Record
Note on N6: SP INSP = Special Inspector Employed by Approved Inspection Agency
Note on O6: TEST LAB = Approved Testing Agency
Note on P6: Additional column may be added here. For large projects attachments may be required to identify all Verified Report Requirements
Note on F23: Aligns with Assembly Bill 2789
Note on F24: Aligns with Assembly Bill 2789

## G-IOR
SECTION G | Inspector of Record (IOR) Responsibility
Facility #: | Facility Name: | Project #:
INSPECTOR OF RECORD RESPONSIBILITIES. Per CAC 7-145: “The Inspector shall have personal knowledge, obtained by continuous inspection of all work of construction in all stages of its progress to ensure that the work is in accordance with the approved construction documents.” This includes applicable Codes, Referenced Standards, Listings and Manufacturer’s Installation Instructions applicable to the work shown in the approved construction documents. If a project has more than one inspector of record, the distribution of responsibilities for the work shall be clearly identified for each IOR per CAC 7-141(f). One IOR shall be designated as the ‘lead’ IOR per CAC 7-144(b). One IOR shall be assigned responsibility for “all other work” to make sure responsibility for the inspection of every part of the work is assigned.
INSPECTOR OF RECORD CAC 7-141, 7-145 & 7-151 | SCOPE OF INSPECTION |  | PERFORMED OFF-SITE
All other work
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## H-Plan Review
SECTION H | HCAI REVIEWED
Facility #: | Facility Name: | Project #:
NOTE: A structural engineer's signature is required for H and I projects or when they are substantially involved on an S project
Submitted By:
I have reviewed the approved construction documents for this project and all tests and special inspections required by Code are marked as “required” on this form.
Architect/Engineer of Record (Print Name) |  | Architect/Engineer of Record (Signature) | Date
Structural Engineer of Record (Print Name) |  | Structural Engineer of Record (Signature) | Date
FOR HCAI USE
TIO Program Reviewed by HCAI Plan Review Staff:
Note: HCAI plan review staff must provide verification that the TIO program has beeen "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## I-TIO Program Approval
SECTION I | TIO PROGRAM APPROVAL
Facility #: | Facility Name: |  | Project #:
This program is prepared and submitted for an OSHPD 2 or OSHPD 5 project. OSHPD 2 projects are limited to construction and remodel projects for: skilled nursing facilities and/or intermediate-care facilities of Type V, wood or light steel-frame construction (2019 CBC 1225.1). OSHPD 5 projects are limited to construction and remodel projects for: acute psychiatric hospitals subject to licensure (2019 CBC 1228.1).
Samples of Test and Inspection Reports are NOT required for tests performed by laboratories approved through OPAA Program
Testing agency qualification for approval or approval of testing agencies shall be through HCAIs OPAA program.
Select one of the following two: OPAA or Certification by Design Professional of Record
OPAA PROGRAM (Provide copy of OPAA program approval for OPAA approved laboratories and testing agencies) or,
Certification by Design Professional of Record - The qualifications, certifications, experience and independence of the approved agencies and individuals named on this form have been evaluated and accepted by the undersigned in accordance with CAC Section 7-141, 7-144 & 7-149; CBC 1703A.1.1 & 1704A.2.1; and ISO 17025 Section 4.1.4 as applicable. Approved agencies and individuals named for structural tests and special inspections have been evaluated and accepted by the structural engineer delegated responsibility for the design and administration of construction of the structural aspects (when such delegation has been made).
Samples (select one of the boxes below. See Section B, C and D for required test and inspection(s))
Samples of Test and Inspection reports to be provided following determination of the responsible firm(s) or individuals. Samples shall be submitted to and approved by the Office prior to proceeding with the work that requires test or special inspections.
Samples attached.
Not applicable. Project has no required test, special inspections or test will be performed by an approved OPAA program.
All test and special inspection reports shall be submitted to the IOR, hospital owner, architect in responsible charge, and the structural engineer by the testing agency per CAC 7-149(a).
Verified compliance reports shall be signed by the individual who performed the special inspection(s) as outlined in CAC 7-151 (c). All reports shall clearly state whether the tests or special inspections were performed in accordance with the HCAI stamped approved documents and whether the results indicate compliance with those documents per CAC 7-149 (a). All IORs performing special inspections shall hold the appropriate certification and equipment, and shall obtain approval from the design professional of record and HCAI prior to performing such work.
NOTE: This Test, Inspection, and Observation Report shall be approved by HCAI field personnel prior to start of construction.
Architect/Engineer of Record (Print Name) |  | Professional License # | Architect/Engineer of Record (Signature) | Date
FOR HCAI FIELD STAFF USE
TIO Program Approved by HCAI Field Staff:
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. HCAI Field staff will issue subsequent "TIO Program Approval". If "Approved with Comments" is checked the following comments shall be resolved by the designer prior to proceeding with the related construction:
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## J-Changes
SECTION J |  | SUMMARY OF CHANGES TO THE TIO PROGRAM NOTE: Note all changes shall be approved as amended construction documents per CAC 7-153, or “concurred with” as non-material alterations per CAC 7-153(b), by HCAI prior to proceeding with the related work.
Facility #: | Facility Name: |  |  | Project #:
TESTING, INSPECTION, AND OBSERVATION PROGRAM NON-MATERIALLY ALTERING CHANGES BY THE ARCHITECT OF RECORD / ENGINEER OF RECORD IN RESPONSIBLE CHARGE |  |  |  |  | HCAI FDD CONCURRENCE (Initial/date)
A signature below indicates that the DPOR has verified the acceptance statements in Section I of this Form are applicable to any approved agencies/testing laboratories and special inspectors added.
REVISION NUMBER | SYNOPSIS OF CHANGE | Architect/Engineer of Record Signature (Initial/date) | Structural Engineer of Record Signature (Initial/date) | DATE of Effective Change
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on D6: Enter a Revision Number for each change to the TIO Form
Note on E6: Brief description of the change to the form
Note on F6: Place initials in the box to indicate the architect or engineer in responsible charge has reviewed and approved the changes
Note on G6: Place initials in the box to indicate the structural engineer has reviewed and approved the changes (not required for changes which don't affect structural)
Note on H6: Effective date of the change

## Revison History
Revision number is shown at Section A, bottom right corner.
Version | Date | Description
R04.0 | 2021-12-08 | Added Phasing
R04.01 | 2021-12-09 | Addressed Cesar's Comments
R04.02 | 2021-12-10 | Updated formatting
R04.03 | 2021-12-10 | Changed phase selection process
R04.04 | 2021-12-15 | Macro revisions for HCAI updating of OSHPD1 and OSHPD2/5 Forms
R04.05 | 2021-12-15 | Addressed Joe's Comments
R04.06 | 2021-12-15 | Removed cell validation on Tab B
R04.07 | 2021-12-16 | Tab B,C,D,E will state if there are no requirements for that phase when printing, instead of not printing sheet.
| • | Fixed bugs
R04.08 | 2021-12-16 | Tab J will print even if no items are included.
R04.09 | 2021-12-22 | Added warning dialogue box when user reduces number of phases.
R04.10 | 2021-12-23 | Added splash screen when printing
| • | Tab G prints with every PDF
| • | Added facility info drop down
| • | Fixed password bug
| • | Fixed Facility Drop Down Function at Startup
R04.11 | 2021-12-27 | Modified facility combo box to seelct text when clicking drop down to allow user to easily delete text for new search
R04.12 | 2021-12-30 | Added screen warning.
| • | Added Facility Number to Facility Name
R04.13 | 2022-01-04 | Updated macro hide rows button to loop over NoPhase
R04.14 | 2022-01-05 | Updated Clear Phase Macro to Work on Tab F
R04.15 | 2021-01-13 | Updated userforms to show on main monitor
| • | Added macro to set print areas when opening spreadsheet
| • | Minor bug fixes
| • | Minor formatting updates
R04.16 | 2021-01-13 | Created demo version for beta testing.
R04.17 | 2021-01-19 | Modified row heights for better printing of tabs H,J,F
| • | Updated Clear TIO macro to fix formatting issues.
R04.18 | 2022-04-05 | Replaced 'Phase' with 'Stage'
R04.19 | 2022-04-19 | Add instructions to each sheet.
R04.20 | 2022-05-05 | Numerous updates based on comments
R04.21 | 2022-05-09 | Updated sheet security
R04.22 | 2022-05-12 | Updated embedded instructions for compatibility with Excel 2013
R04.23 | 2022-05-16 | Coordinated TIO items with Master List
R04.24 | 2022-06-03 | Minor text and grammar updates on macro instructions.
| • | Updated OSHPD to HCAI on TIO Flowchart
R04.25 | 2022-10-11 | Added missing facilities to drop down
| • | Added C-OT3 and C-OT4 on OSHPD 2/5
| • | Fixed drop down since some facilities were not showing up.
R04.26 | 2023-08-18 | Updated print area to include column headings on each page