## A-Project Info
Testing, Inspection, and Observation Program
2022 California Building Standards Code OSHPD 1
This program is prepared and submitted for an OSHPD 1 project. OSHPD 1 projects include all construction and remodel projects for: general acute care hospitals, acute psychiatric hospitals, and general acute care hospitals providing only acute medical rehabilitation center services (CBC 1224.1).
SECTION A |  | PROJECT INFORMATION
Facility #: | Facility Name: |  | Project #:
Street Address:
City: |  | County:
Record Name (Scope of Project):
Abbreviations:
CAC: California Administrative Code |  | AAMA: American Architectural Manufacturers Association
CBC: California Building Code |  | NFPA: National Fire Protection Association
CEC: California Electrical Code |  | FM: FM Approval Standards
CMC: California Mechanical Code |  | DPOR: Design Professional of Record
CPC: California Plumbing Code
Testing, Inspection, and Observation Stages
Stage No. | Stage Name | Stage Scope / Description
1
DESIGN PROFESSIONAL OF RECORD RESPONSIBILITY
The administration of the work of construction, including this TIO, shall be under the responsible charge of an architect and structural engineer. When a structural engineer is not substantially involved, the architect shall be solely responsible. Where neither structural nor architectural elements are substantially involved, a mechanical or electrical engineer registered in the branch of engineering most applicable to the project may be in responsible charge. (CAC 7-141(a))
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
The "TIO Program Approval" from HCAI field staff must be obtained and included with the notice of start of construction required by CAC Section 7-137(a)4) and 7-145(a)5.A)
Construction shall not commence until the health facility has obtained from HCAI "TIO Program Approval". (CAC Section 7-135(a)3)
Note on I12: Project Number – As assigned by HCAI
Note on G15: Record Name (Scope of Project) – Scope of the project, as shown on the Application for New Project
Note on D23: TIO Stage Description - Provides a name and description/scope for each stage of a TIO program. Select the number of stages for your project by using the list box to the right of the project stage description. If the TIO program will be administered in a single stage then select "1 Stage". The number of stages on Tabs A, B, C, and D will automatically update when the number of stages is selected in the list box.

## B-Tests
|  |  | SECTION B |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | #NAME? |  | #NAME? | #NAME?
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | TESTS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Individual) | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
x1 | Structural
| x1s1 | Foundation
|  |  | B-F1 |  | Soil fill CBC 1705A.6 Fill material acceptance test
|  |  | B-F2 |  | Soil fill CBC 1705A.6 Compaction test
|  |  | B-F3 |  | Soil and rock anchors CBC 1811A Load test
|  |  | B-F4 |  | Deep foundation elements CBC 1810A.3.1.5.1, 1810A.3.3.1.2, 1810A.3.3.1.5, 1810A.3.3.2, & 1810A.3.10.4 Load test
|  |  | B-F5 |  | Shoring CBC 1812A Tie-Back Anchors
|  |  | B-F6 |  | Vibro Stone Columns (VSC) CBC 1813A Acceptance Test
| x1s2 | Concrete
|  |  | B-C1 |  | Concrete Mix Components CBC 1705A.3, 1903A.6 & 1910A.1; ACI 318 1.9.1 & 26.4.1.1 Cementitious materials
|  |  | B-C2 |  | Concrete Mix Components CBC 1705A.3, 1903A.5; ACI 318 1.9.1 & 26.4.1.2 Aggregates/Reactive aggregates
|  |  | B-C3 |  | Concrete Mix Components CBC 1705A.3; ACI 318 26.4.1.4; ASTM C1602 Water
|  |  | B-C4 |  | Concrete Strength Test CBC 1705A.3 & 1905A.1.17; ACI 318 26.12 Strength test for concrete and high-strength grout
|  |  | B-C5 |  | Cast-In Components CBC 1705A.3 & 1910A.2; ACI 318 20.2, 25.4.5.1 & 26.6.1.2 Metal reinforcement (including welded wire fabric and headed rebar)
|  |  | B-C6 |  | Cast-In Components CBC 1705A.3, 1901A.3; ACI 318 20.4 Headed studs and headed stud assemblies
|  |  | B-C7 |  | Cast-In Components CBC Table 1705A.3, 1903A.8 Weldability of reinforcing bars
|  |  | B-C8 |  | Prestressed Concrete CBC 1705A.3 & 1910A.3; ACI 318 20.3, 25.8 & 26.6.1.2 Prestressing tendons and anchorage
|  |  | B-C9 |  | Strengthening and Repair CBC 1911A.2; ACI 503.7 Crack repair by epoxy injection
|  |  | B-C10 |  | Strengthening and Repair CBC 1911A.3; ICC-ES AC 178 Sect 9 Strengthening by externally bonded FRP
|  |  | B-C11 |  | Shotcrete CBC 1705A.3.9.2 & 1908A.2 Preconstruction test
|  |  | B-C12 |  | Shotcrete CBC 1705A.3.9 & 1908A.2 Strength test
|  |  | B-C13 |  | Post-installed anchors CBC 1910A.5 Installation verification test (includes adhesive, shot pins and mechanical anchors)
|  |  | B-C14 |  | Existing Post-Installed Anchors CBC 1708A and CAC Ch 6, Sect 11.3 In-situ load tests
| x1s3 | Masonry
|  |  | B-MA1 |  | Mortar and Grout CBC 2105A.3 Mortar test
|  |  | B-MA2 |  | Mortar and Grout CBC 2105A.3 Grout test
|  |  | B-MA3 |  | Masonry Strength Test CBC 2105A.2; TMS 602 1.4.B.3 Compressive strength prism test (f'm)
|  |  | B-MA4 |  | Masonry Strength Test CBC 2105A.4 Core tests of masonry wall samples
|  |  | B-MA5 |  | Post-Installed Anchors in Masonry CBC 1705A.4 Installation verification test
|  |  | B-MA6 |  | Veneer CBC 1410.2 Veneer bond strength test
|  |  | B-MA7 |  | Architectural Cast Stone CBC 2103A.1; ASTM C1354 Strength of stone anchorage
| x1s4 | Steel
|  |  | B-S1 |  | Steel Identification CBC Table 1705A.2.1 & 2202A.1 Testing of unidentified steel or identification test for structural steel and cold formed steel
|  |  | B-S2 |  | Steel Components CBC 2213A.1 & 1705A.2.6 High strength bolts, nuts, and washers
|  |  | B-S3 |  | Steel Components CBC 2213A.2 & 1705A.2.5 End-welded studs
|  |  | B-S4 |  | Welds CBC 1705A.2.5 Nondestructive testing of welds
|  |  | B-S5 |  | Seismic Force Resisting System CBC 2205A.4 & 1705A.14.1 Nondestructive tests for seismic resistance
| x1s5 | Other Structural Materials
|  |  | B-OM1 |  | Aluminum CBC 2003.1 Testing
|  |  | B-OM2 |  | Structural Sealant Glazing CBC 2410.1.2; AAMA 501.4; AAMA 501.6 Exterior glass curtain walls tests
|  |  | B-OM3 |  | Thermal Barriers in Aluminum Mullion Systems CBC 2411.1.2 Testing of thermal barriers
| x1s6 | Alternative Systems
|  |  | B-AS1 |  | Seismic Isolation System CBC 1705A.14.4 Prototype and production test
|  |  | B-AS2 |  | Seismic Damping System CBC 1705A.14.4 Prototype and production test
|  |  | B-AS3 |  | Structural Design Criteria CBC 104.11.2 Tests to support alternative system
|  |  | B-AS4 |  | Wind Tunnel Testing CBC 1609A.1.1; ASCE 7 31.4 & 31.5; ASCE 49 Wind tunnel testing
| x1s7 | Nonstructural Components, Supports and Attachments
|  |  | B-N1 |  | Special Seismic Certification CBC 1705A.14.3 Shake table test
| x1s8 | User Defined Structural Tests
B-SU01
B-SU02
x2 | Architectural
| x2s1 | Radiation Shielding Barriers
|  |  | B-AT1 |  | Radiation shielding barrier test CBC 1705A.1.1 and 3102C
| x2s2 | User Defined Architectural Tests
B-AU01
B-AU02
x3 | Mechanical
| x3s1 | Ventilation and Pressurization
|  |  | B-ME1 |  | Listed Hood Assemblies CMC 508.2
|  |  | B-ME2 |  | Type I Hood Capture and Containment Test CMC 511.2.2.2
|  |  | B-ME3 |  | Commercial Kitchen Hood Ventilation CMC 511.2.2.1 Performance test
|  |  | B-ME10 |  | Pre-Demolition Air Balance CMC 407.3.1 Air balance test and report
|  |  | B-ME11 |  | Post-Demolition Air Balance CMC 407.3.1 Air balance test and report
|  |  | B-ME12 |  | Ventilation System Air Balance CMC 407.3.1, Table 4-A Areas tested and balanced
|  |  | B-ME13 |  | Infection Control Planning and Protection ASHRAE 170-2013 8.4 Infection control risk assessment and protection procedure development
|  |  | B-ME14 |  | Duct Leakage Test CMC 603.9.2 SMACNA HVAC air duct leakage test
|  |  | B-ME15 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 416.4 Alarm system test
|  |  | B-ME16 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 417.0 Mechanical system tested and balanced
| x3s2 | Refrigeration Machinery
|  |  | B-ME4 |  | Refrigeration Equipment CMC 1116.0
|  |  | B-ME5 |  | Refrigeration Detection and Alarm System CMC 1108.4 & CFC 608.7 Acceptance testing
|  |  | B-ME6 |  | Refrigeration Flaring System CMC 1114.3 Safety and effectiveness
| x3s3 | Boilers/Piping
|  |  | B-ME7 |  | Steam and Hot Water Boilers CMC 1013.0
|  |  | B-ME8 |  | Hydronics CMC 1205.2, 1220.4.6 & 1221.3 Pressure test of steam and water piping
|  |  | B-ME9 |  | Process Piping CMC 1405.2.2 Pressure test
| x3s4 | User Defined Mechanical Tests
B-MU01
B-MU02
x4 | Electrical
| x4s1 | Service and Feeders 1000A or More
|  |  | B-E1 |  | Ground Fault Protection of Equipment CEC 230.95(C) & 517.17(D)
| x4s2 | Essential Power Systems
|  |  | B-E2 |  | Emergency Systems/Generator Tests CEC 700.3(A) & NFPA 110-2019 Sect 7.13
|  |  | B-E3 |  | Automatic Transfer Switch Test 2019 NFPA 110 Sect 7.13.4.1
|  |  | B-E4 |  | Emergency Stored Electrical Energy System Test 2019 NFPA 111 Sect 7.6
|  |  | B-E15 |  | Means of Egress Illumination CBC 1008.2 & 1008.3 Illumination and emergency power
| x4s3 | Patient Care Spaces
|  |  | B-E5 |  | Grounding System in Patient Care Spaces 2021 NFPA 99 6.3.3.1
|  |  | B-E6 |  | Hospital Grade Receptacles 2021 NFPA 99 6.3.3.2.5
|  |  | B-E7 |  | Isolated Power Systems – Line Isolation Monitor Test 2021 NFPA 99 6.3.3.3.2
|  |  | B-E8 |  | Isolated Power Systems – Impedance of Isolated Wiring Test 2021 NFPA 99 6.3.2.9.2.1
| x4s4 | Medium Voltage Systems
|  |  | B-E9 |  | Medium Voltage Outdoor Systems Testing CEC 225.56
|  |  | B-E10 |  | Medium Voltage Cable Testing CEC 311.30, 225.56 & ANSI/NECA/NCSCB 600-2014
| x4s5 | Wiring
|  |  | B-E11 |  | Insulation Testing CEC 110.7
|  |  | B-E12 |  | Torque Electrical Connections CEC 110.3(B) & 110.14(D)
| x4s6 | Low Voltage Systems
|  |  | B-E14 |  | Nurse Call System CEC 517.123
| x4s7 | User Defined Electrical Tests
B-EU01
B-EU02
x5 | Plumbing
| x5s1 | Water Supply
|  |  | B-P1 |  | Disinfection of Potable Water Systems CPC 609.10
|  |  | B-P9 |  | Water Supply System CPC 105.3 & 609.4 Pressure tested prior to covering or concealment
|  |  | B-P18 |  | Backflow Prevention Devices and Assemblies CPC 603.2 & 603.4.2 Assembly tested
|  |  | B-P19 |  | Non-Potable Water CPC 1502.0 Testing of alternate water sources and cross-connections
|  |  | B-P20 |  | Recycled Water Supply Systems CPC 1505.5 & 1505.13 Initial cross-connection test and system testing before initial operation
|  |  | B-P21 |  | On-Site Treated Non-Potable Gray Water Systems CPC 1502.1, 1506.5, & 1506.12 Initial cross-connection test and system testing before initial operation
| x5s2 | Medical Gases
|  |  | B-P2 |  | Medical Gas and Vacuum NFPA 99-2021 Sect 5.1.10.11.11 Qualification of brazing procedures and brazing
|  |  | B-P3 |  | Medical Gas and Vacuum NFPA 99-2021 Sect 5.1.12.2.1 thru 5.1.12.2.7 Installer performed tests |  |  | ASSE 6010 Cert Req'd
|  |  | B-P4 |  | Medical Gas and Vacuum NFPA 99-2021 Sect 5.1.12.2.6.7 & 5.1.12.2.7.6 Witness of 24-hour standing pressure test |  |  | ASSE 6020 or 6030 Cert Req'd or Qualified IOR
|  |  | B-P5 |  | Medical Gas and Vacuum NFPA 99-2021 Sect 5.1.12.3.1.1 thru 5.1.12.3.1.5 System inspection prior to concealment/cover |  |  | ASSE 6020 or 6030 Cert Req'd
|  |  | B-P6 |  | Medical Gas and Vacuum NFPA 99-2021 Sect 5.1.12.3.2.1 Inspection |  |  | ASSE 6020 or 6030 Cert Req'd or Qualified IOR
|  |  | B-P7 |  | Medical Gas and Vacuum NFPA 99-2021 Sect 5.1.12.4 System verification |  |  | ASSE 6030 Cert Req'd
| x5s3 | Drainage
|  |  | B-P8 |  | Existing Sewers and Drains CPC 102.4.1, 105.3, & 712.0 Tested for conformance with requirements for new work
|  |  | B-P10 |  | Plumbing, Drainage, and Venting Systems CPC 105.3 & 712.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P11 |  | Building Sewer CPC 105.3, 712.0, & 723.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P12 |  | Storm Drain Piping CPC 1107.0 Water or air tested prior to use, covering or concealment
|  |  | B-P14 |  | Private Sewer Disposal System CPC 105.0, & CPC Appendix H H1001.2 Tested prior to use, covering, or concealment
|  |  | B-P16 |  | Defective Systems CPC 105.3.1, 105.3.2, 712.0 Air test of defective drainage and plumbing systems
|  |  | B-P17 |  | Shower Receptors CPC 408.7.5
| x5s4 | Fuel Gas
|  |  | B-P13 |  | Fuel Gas Piping CPC 1213.0 & CMC 1313.0 Air, CO2 or nitrogen tested prior to use, covering, or concealment
| x5s5 | Coated Pipe
|  |  | B-P15 |  | Protectively Coated Pipe CPC 312.5 Tested for voids, damage, and imperfections
| x5s6 | User Defined Plumbing Tests
B-PU01
B-PU02
x6 | Fire Protection and Life Safety System
| x6s1 | Fire Alarm
|  |  | B-FP1 |  | Fire Alarm CFC 901.5 & CFC 907.7 NFPA 72-2022 Sect 14.4 Acceptance and reacceptance testing
| x6s2 | Fire and Smoke Dampers
|  |  | B-FP2 |  | Fire and Smoke Dampers CFC 901.5 & CFC 907.8 Acceptance testing
| x6s3 | Duct Detectors
|  |  | B-FP3 |  | Duct Detectors CFC 901.5, NFPA 72-2022 Sect 14.4 Differential pressure test
| x6s4 | Smoke Control System
|  |  | B-FP4 |  | Smoke Control System CFC 901.5, CFC 909.18 & 1705A.19 Acceptance testing
| x6s5 | Sprinklers
|  |  | B-FP5 |  | Fire Sprinkler CFC 901.5 & NFPA 13-2022 Chapter 29 Above ground piping acceptance testing
|  |  | B-FP6 |  | Fire Sprinkler CFC 901.5 & NFPA 13-2022 Chapter 29 Underground piping acceptance testing
| x6s6 | Standpipe Systems
|  |  | B-FP7 |  | Standpipe Systems CFC 901.5 & NFPA 14-2019 Chapter 11 Above ground piping acceptance testing
|  |  | B-FP8 |  | Standpipe Systems CFC 901.5, CFC 905.3.1 & NFPA 14-2019 Chapter 11 Acceptance testing in buildings 4-stories or more
|  |  | B-FP9 |  | Standpipe Systems CFC 901.5 & NFPA 14-2019 Chapter 11 Underground piping acceptance testing
| x6s7 | Private Fire Mains
|  |  | B-FP10 |  | Private Fire Mains CFC 901.5 & NFPA 24-2019 Sect 10.10 Acceptance testing
| x6s8 | Fire Pumps
|  |  | B-FP11 |  | Fire Pumps CFC 901.5 & NFPA 20-2019 Sect 14.1 & 14.2 Acceptance testing
| x6s9 | Fire Protection Water Tank
|  |  | B-FP12 |  | Fire Protection Water Tank CFC 901.5 & NFPA 22-2018 Chapter 17 Acceptance testing
| x6s10 | Alternative Automatic Fire Extinguishing Systems
|  |  | B-FP13 |  | Wet Chemical Extinguishing System CFC 901.5 & NFPA 17A-2021 Sect 7.4 Acceptance testing
|  |  | B-FP14 |  | Clean Agent Extinguishing System CFC 901.5 & NFPA 2001-2018 Sect 7.7 Acceptance testing
|  |  | B-FP15 |  | CO2 Extinguishing System CFC 901.5 & NFPA 12-2018 Sect 4.4.3 & 4.4.4 Acceptance testing
|  |  | B-FP16 |  | Dry Chemical Extinguishing System CFC 901.5 & NFPA 17-2021 Sect 10.4 Acceptance testing
|  |  | B-FP17 |  | Halon 1301 Extinguishing System CFC 901.5 & NFPA 12A-2018 Sect 6.7 Acceptance testing
| x6s11 | Fuel Tanks
|  |  | B-FP18 |  | Underground Fuel Storage Tank CFC 5704.2.12 & NFPA 30-2021 Sect 21.5.1 Initial testing
|  |  | B-FP19 |  | Underground Fuel Storage Tank CFC 5704.2.12 & NFPA 30-2021 Sect 21.5.2 Tightness testing
|  |  | B-FP20 |  | Flammable and Combustible Liquid Fuel Piping CFC 5703.6.3 Pressure testing
| x6s12 | Emergency Responder Radio Coverage
|  |  | B-FP21 |  | Emergency Responder Radio Coverage CFC 510.5.4 Acceptance test procedure
| x6s13 | Elevators
|  |  | B-FP22 |  | Testing of Elevator Shutdown CBC 3005.5, NFPA 72-2022 21.4, & ASME A17.1/CSA B44-2019
|  |  | B-FP23 |  | Elevator Emergency Operation CBC 3003.2 Emergency recall and in-cart operation
|  |  | B-FP24 |  | Elevator Emergency Standby Power CBC 3003.1 Backup generator engaged
| x6s14 | Fire Door, Fire Shutter, and Fire Windows
|  |  | B-FP25 |  | Fire Door, Fire Shutter, and Fire Windows NFPA 80-2019 5.2 Testing
| x6s15 | Fire Watch
|  |  | B-FP26 |  | Fire Watch CBC 901.7 & CAN 9-901.7 Review of the fire watch log and the written sign off / permission to terminate fire watch.
| x6s16 | User Defined Fire Protection and Life Safety System Tests
B-FU01
B-FU02
x7 | OTHER
| x7s1 | User Defined Tests
B-OU01
B-OU02
B-OU03
B-OU04
B-OU05
B-OU06
B-OU07
B-OU08
B-OU09
B-OU10
x8 | END OF TESTS
Note on F44: Required for projects that use aluminum as a structural material.
Note on F45: Required for projects that include glazing scope that uses structural sealant.
Note on F46: This is for HCAI 1, 1R, 2, 4 & 5. The requirements of this section address the testing and inspection of thermal barriers composite in aluminum mullion systems.
Note on F48: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F49: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F50: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F53: Required on projects where equipment requiring special seismic certification has not been preapproved or justified by analysis.
Note on F59: Required on all projects that contain imaging equipment radiation shielding barriers.
Note on F65: Listed hood assemblies shall be tested in accordance with UL 710 or equivalent. Listed UV hood assemblies shall be tested in accordance with UL 710 or UL 710C.
Note on F66: Listed hood assemblies shall be tested per manufacturer. Listed UV hoods tested IAW UL 710 and 710C.
Note on F67: Performance test before final approval of install of ventilation system.
Note on F68: Survey of existing ventilation system priory to start of remodel work.
Note on F69: Survey of ventilation system at completion of remodel work to ensure pre-demolition air balance values are maintained.
Note on F70: Test and balance of new spaces, spaces affected by new equipment or spaces with change in function after completion of work.
Note on F71: For projects that modify or remodel HVAC systems in an existing facility.
Note on F73: Testing of air pressure alarm systems prior to acceptance.
Note on F74: Test and balance of mechanical system after completion of work.
Note on F76: Factory and field refrigeration system pressure testing.
Note on F77: Alarm system testing of machinery room alarm systems.
Note on F78: Report for approved agency detailing emission products.
Note on F80: Inspection and test protocol for boilers after installation and prior to use.
Note on F81: Pressure testing for system piping and components. Note: piping to be installed in concrete shall be tested per these requirements prior to pouring concrete.
Note on F82: Pressure test at completion of installation.
Note on F88: For 480V electrical "service" rated 1000A or more, and a feeder meeting CEC 215.10. (NOT FOR GFCI TESTING).
Note on F90: For new and replacement emergency generator installations.
Note on F91: For new and replacement automatic transfer switch installations.
Note on F92: Testing of UPS and other battery storage systems used as energy storage system. Note: An UPS supplied by an emergency power supply system (EPSS) like an essential electrical system is not required to be tested to NFPA 111.
Note on F95: Voltage and impedance measurements when new electrical circuits and receptacles are installed in patient care spaces like head walls.
Note on F96: Receptacle retention force test when new receptacles are installed in patient care spaces like head walls
Note on F97: For Operating Room / Wet Procedures with isolated power systems.
Note on F98: For Operating Room / Wet Procedures with isolated power systems.
Note on F100: Medium voltage (over 1000v) may be used for a large hospital campus. Pre-energization and operational tests for new and modified electrical systems over 1000V.
Note on F101: Testing of new medium volt cables (1kv - 100kv). Related to Medium Voltage Outdoor Systems – Inspections and Test.
Note on F103: Megger test of new conductors to ensure wiring is free from short circuits and ground faults.
Note on F104: For panelboards, switchboards, switchgear, MCC, and other electrical equipment that require electrical connections to be torqued per manufacture instructions.
Note on F106: For new or modified nurse call systems. This is a functional test.
Note on F112: Testing to be done for new piping and when pipes have been breached in project. Not for fixture replacement.
Note on F113: Testing of completion of new segment or entire system.
Note on F114: Device shall be approved by the AHJ and then tested at time of installation, repair, or relocation.
Note on F115: Testing of all new alternate water sources for non-potable water including testing emphasis on cross-connection prevention.
Note on F119: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F120: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems by a responsible entity with ASSE 6010 certification.
Note on F121: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems by a responsible entity with ASSE 6020 or 6030 certification, or a qualified IOR.
Note on F122: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems by a responsible entity with ASSE 6020 or 6030 certification.
Note on F123: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems by a responsible entity with ASSE 6020 or 6030 certification, or a qualified IOR.
Note on F124: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems by a responsible entity with ASSE 6030 certification.
Note on F126: Testing for modified or breached sewer piping.
Note on F129: Water or air testing for new storm drain piping, and parts of existing storm drain piping that have been altered, extended, or repaired.
Note on F130: Static and fluid water testing after installation.
Note on F131: Air testing of existing drainage or plumbing that is suspected to be defective.
Note on F132: Standing water test for drain/receptor interface.
Note on F134: Testing required for new, or repaired fuel piping prior to acceptance and initial operation.
Note on F142: For new installations, remodels, replacements or repairs. When required, test when interconnected with other systems. and before the occupancy of the building or specific area.
Note on F144: Shall be tested when the system is altered or modified. When required, test when interconnected with other systems.
Note on F146: For new installations, remodels, replacements, repairs, or when there are changes to the site-specific software. When required, test when interconnected with other systems. Shall notify HCAI and owner prior to initial acceptance test.
Note on F148: For new installations, remodels, replacements or repairs. When required, test when interconnected with other systems. Test shall include function, sequence and, where applicable, capacity of their installed condition. Test shall be prior to concealment and prior to occupancy.
Note on F150: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F151: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F153: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independently. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F154: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independently. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F155: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independently. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F157: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F159: For new installations, remodels, replacements or repairs. If components that affect performance are replaced, then a retest shall be conducted by the pump manufacturer or designated representative or qualified persons acceptable to HCAI.
Note on F161: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test. Prior to placing the tank in service, a representative of the tank contractor and a representative of the owner shall conduct a joint inspection of the completed equipment.
Note on F163: For new installations, remodels, replacements or repairs.
Note on F164: For new installations, remodels, replacements or repairs.
Note on F165: For new installations, remodels, replacements or repairs.
Note on F166: For new installations, remodels, replacements or repairs.
Note on F167: For new installations, remodels, replacements or repairs.
Note on F169: For new installations, remodels, replacements or repairs.
Note on F170: For new installations, remodels, replacements or repairs.
Note on F171: For new installations, remodels, replacements or repairs.
Note on F173: For new installations, remodels, replacements or repairs.
Note on F175: For new installations, remodels, replacements or repairs.
Note on F176: For new installations, remodels, replacements or repairs.
Note on F177: For new installations, remodels, replacements or repairs.
Note on F179: For new installations, remodels, replacements or repairs.

## C-On-Site Special Inspections
|  |  | SECTION C |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | #NAME? |  | #NAME? | #NAME?
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | ON-SITE SPECIAL INSPECTIONS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Special Inspector) | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
x1 | Structural
| x1s1 | Foundation
|  |  | C-F1 |  | Soils CBC 1705A.6 Soil fill
|  |  | C-F2 |  | Soils CBC 1705A.6 Bearing capacity of materials below shallow foundations
|  |  | C-F3 |  | Soils CBC 1705A.6 Excavation depth
|  |  | C-F4 |  | Deep Foundations CBC 1705A.7 Driven deep foundations
|  |  | C-F5 |  | Deep Foundations CBC 1705A.8 Cast-in-place deep foundations
|  |  | C-F6 |  | Deep Foundations CBC 1705A.9 Helical pile foundations
|  |  | C-F7 |  | Shoring CBC 1812A Shoring
|  |  | C-F8 |  | Vibro Stone Columns (VSC) CBC 1813A Vibro stone columns
|  |  | C-F9 |  | Prestressed Soil and Rock Anchors CBC 1811A & 1812A Installation and testing
| x1s2 | Concrete
|  |  | C-C2 |  | Concrete Installation CBC 1705A.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | C-C3 |  | Concrete Mix and Mix Components CBC 1705A.3; ACI-318 26.4.1.5 Admixtures
|  |  | C-C4 |  | Concrete Mix and Mix Components CBC 1705A.3; ACI-318 26.4 Mix design
|  |  | C-C5 |  | Post-Installed and Cast-In Components CBC 1705A.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | C-C6 |  | Post-Installed and Cast-In Components CBC 1705A.3 CIP & post-installed anchors
|  |  | C-C7 |  | Post-Installed and Cast-In Components CBC Table 1705A.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | C-C8 |  | Post-Installed and Cast-In Components CBC 1705A.3; ACI-318 26.13 Specialty inserts, stud rails, rebar mechanical connections, headed rebar
|  |  | C-C9 |  | Prestressed Concrete CBC 1705A.3.4; ACI-318 26.13
|  |  | C-C10 |  | Precast Concrete Erection CBC 1705A.3; ACI 318 26.9, 26.13.1 & 26.13.3.3
|  |  | C-C11 |  | Shotcrete CBC 1705A.3.9 & 1908A Installation
|  |  | C-C12 |  | Insulating Concrete CBC 1705A.3
|  |  | C-C13 |  | Post-Installed and Cast-In Components CBC 1705A.3, 1705A.3.1 & 1903A.8 Welding of reinforcing bars
|  |  | C-C14 |  | GFRC Panels PCI MNL 128 standard
|  |  | C-C15 |  | Strengthening and Repair CBC 1911A.2; ACI 503.7 Crack repair by epoxy injection
|  |  | C-C16 |  | Strengthening and Repair CBC 1911A.3, ICC AC178 Sect 3 to 8 Strengthening by externally bonded FRP
| x1s3 | Masonry
|  |  | C-MA1 |  | Masonry Construction CBC 1705A.4 Laying and grouting
|  |  | C-MA2 |  | Masonry Construction CBC 2104A.1.3 Reinforced grouted masonry
|  |  | C-MA3 |  | Post-Installed and Cast-In Components in Masonry CBC 1705A.4 CIP & post-installed anchors
| x1s4 | Steel
|  |  | C-S2 |  | Welding CBC 1705A.2.1 & 1705A.2.5 Automatic End-Welded Studs
|  |  | C-S3 |  | Welding CBC 1705A.2.5 Weld Inspections
|  |  | C-S4 |  | Welding AWS D1.1 3 & 4, and AWS D1.8 6.1 WPS / WPQR
|  |  | C-S5 |  | High Strength Bolt Installation CBC 1705A.2 & 1705A.2.6
|  |  | C-S6 |  | Cold-Formed Steel Light Frame Construction CBC 1705A.2, 1705A.12.2, & 1705A.13.3
|  |  | C-S7 |  | Special Inspections for Seismic Resistance CBC 1705A.13.1.1 & 1705A.13.1.2 Seismic force-resisting systems and elements
| x1s5 | Wood
|  |  | C-W1 |  | Glue Laminated Timber CBC 1705A.5, 1705A.5.5, & 1705A.12.1
|  |  | C-W2 |  | Timber Connector Installation CBC 1705A.5.6, 1705A.11.1, & 1705A.12.1
|  |  | C-W3 |  | Manufactured Trusses CBC 1705A.5, 1705A.5.2, & 1705A.5.6
|  |  | C-W4 |  | Fastening CBC 1705A.12.1 & 1705A.13.2 Nailing, screw attachment, bolting, anchoring, field gluing operations, and other fastening
| x1s6 | Other Structural Materials
|  |  | C-OM1 |  | Aluminum CBC 2003.1 Inspection
|  |  | C-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 & 1705A.13.5.2 Structural sealants for exterior glass curtain walls
|  |  | C-OM3 |  | Thermal Barriers in Aluminum Mullion Systems CBC 2411.1.2 Testing and inspection
| x1s7 | Alternative Systems
|  |  | C-AS1 |  | Alternative system CBC 1705A.1.1 Construction materials and methods for alternative system
|  |  | C-AS2 |  | Seismic Isolation System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
|  |  | C-AS3 |  | Seismic Damping System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
| x1s8 | Nonstructural components, supports and attachments
|  |  | C-N1 |  | Nonstructural Walls and Components CBC 1705A.13.5 & 1705A.17 Cladding, nonbearing walls, and veneer
|  |  | C-N2 |  | Ceiling CBC 1705A.13.5 Suspended ceiling systems and their anchorage
|  |  | C-N3 |  | Access Floors CBC 1705A.13.5.1 Anchorage of access floor systems
|  |  | C-N4 |  | Storage Racks 8 ft or Taller CBC 1705A.13.7 Anchorage
|  |  | C-N5 |  | Mechanical, Electrical, and Plumbing Components CBC 1705A.13.6 Anchorage, bracing, and vibration isolators
|  |  | C-N6 |  | Special Seismic Certification CBC 1705A.13.4 Special seismic certification label, anchorage, and mounting
| x1s9 | User Defined Structural Special Inspections
C-SU01
C-SU02
x2 | Mechanical
| x2s1 | User Defined Mechanical Special Inspections
C-MU01
C-MU02
x3 | Electrical
| x3s1 | Adjustable Overcurrent Protection Devices
|  |  | C-E1 |  | Available Fault and Short-Circuit Current Field Marking per Approved Coordination Study CEC 110.16(B), 409.110, 430.98, 620.51(D)(2) & 700.5(E)
|  |  | C-E2 |  | Essential Electrical System OCPD Selection and Adjustable Settings Check per Approved Coordination Study CEC 517.31(G)
|  |  | C-E3 |  | Elevator Circuit Breaker Selection and Settings per Approved Coordination Study CEC 620.62
| x3s2 | Fire Pumps
|  |  | C-E4 |  | Fire Pump Circuit Breaker Selection and Settings per Approved Coordination Study CEC 695.3(C)(3)
| x3s3 | Labeling
|  |  | C-E6 |  | Arc Flash Hazard Warning CEC 110.16(A)
| x3s4 | User Defined Electrical Special Inspections
C-EU01
C-EU02
x4 | Plumbing
| x4s1 | User Defined Plumbing Special Inspections
C-PU01
C-PU02
x5 | Fire Protection and Life Safety System
| x5s1 | Fireproofing and Fire Stopping
|  |  | C-FP1 |  | Sprayed Fire-Resistant Materials CBC 1705A.15 Spray-applied fireproofing
|  |  | C-FP2 |  | Mastic and Intumescent Fire-Resistant Coatings CBC 1705A.16 In accordance with AWCI 12-B
|  |  | C-FP3 |  | Penetration Firestops CBC 1705A.18.1 Penetration firestop systems that are tested and listed
|  |  | C-FP4 |  | Fire-Resistant Joint Systems CBC 1705A.18.2 Fire-resistant joint systems that are tested and listed
| x5s2 | Smoke Control Systems
|  |  | C-FP5 |  | Smoke Control Systems CFC 909.18.8, CBC 1705A.14.3.1, & 1705A.19 Ductwork and operation
| x5s3 | Sprinklers
|  |  | C-FP6 |  | Sprinkler System Piping NFPA 13-2022 Sect 7.5.2 Welded pipe and fittings
| x5s4 | Standpipe Systems
|  |  | C-FP7 |  | Standpipe System Piping NFPA 14-2019 Sect 4.4.2 Welded pipe and fittings
| x5s5 | Fire Door, Fire Shutter, and Fire Windows
|  |  | C-FP8 |  | Fire Door, Fire Shutter, and Fire Windows NFPA 80-2019 5.1.4, 5.2 Inspection and labeling
| x5s6 | Portable Fire Extinguishing Equipment
|  |  | C-FP9 |  | Portable Fire Extinguishers CFC 906 & CCR, Title 19, Division 1, Sect 3.29(a)-(d)
| x5s7 | Exterior Finish Systems
|  |  | C-FP10 |  | Exterior insulation and finish systems (EIFS) CBC 1705A.17 EIFS applications
| x5s8 | User Defined Fire Protection and Life Safety System Special Inspections
C-FU01
C-FU02
x6 | Architectural
| x6s1 | Exterior Finish Systems
|  |  | C-A2 |  | Water-Resistive Barrier Coating CBC 1705A.17.1 ASTM E2570 barrier coating when installed over a sheathing substrate
| x6s2 | Signage
|  |  | C-A3 |  | Exit Signs CBC 1013.1 Location, illumination and physical characteristics
|  |  | C-A4 |  | Accessible Signage CBC 11B-703.1 Visual and tactile requirements
| x6s3 | Roof Coverings
|  |  | C-A5 |  | Substrate for Roof Coverings CBC 1507 Requirements for Roof Coverings
|  |  | C-A6 |  | Installation of Roof Coverings CBC 1506 Materials
| x6s4 | User Defined Architectural Special Inspections
C-AU01
C-AU02
x7 | Non-Residential Certificate Of Acceptance (NRCA)
| x7s1 | Covered Processes
|  |  | C-NRCA1 |  | Compressed Air California Energy Code 2022-CEC-NRCA-PRC-01-F: https://www.energy.ca.gov/filebrowser/download/4913 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA2 |  | Escalator Speed Control California Energy Code 2022-CEC-NRCA-PRC-13-F: https://www.energy.ca.gov/filebrowser/download/4922 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA3 |  | Parking Garage Ventilation California Energy Code 2022-CEC-NRCA-PRC-03-F: https://www.energy.ca.gov/filebrowser/download/4915 |  |  | Responsible Designer Or Installing Contractor
| x7s2 | Envelope
|  |  | C-NRCA4 |  | Fenestration Acceptance California Energy Code 2022-CEC-NRCA-ENV-02-F: https://www.energy.ca.gov/filebrowser/download/4942 |  |  | Responsible Designer Or Installing Contractor
| x7s3 | Lighting
|  |  | C-NRCA5 |  | Automatic Daylighting Control California Energy Code 2022-CEC-NRCA-LTI-03-A: https://www.energy.ca.gov/filebrowser/download/5066 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA6 |  | Demand Response Controls California Energy Code 2022-CEC-NRCA-LTI-04-A: https://www.energy.ca.gov/filebrowser/download/5067 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA7 |  | Institutional PAF California Energy Code 2022-CEC-NRCA-LTI-05-A: https://www.energy.ca.gov/filebrowser/download/5068 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA8 |  | Outdoor Lighting Controls California Energy Code 2022-CEC-NRCA-LTO-02-A: https://www.energy.ca.gov/filebrowser/download/5069 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA9 |  | Shut-Off Lighting Control California Energy Code 2022-CEC-NRCA-LTI-02-A: https://www.energy.ca.gov/filebrowser/download/5065 |  |  | Responsible Designer Or Installing Contractor
| x7s4 | User Defined Non-Residential Certificate Of Acceptance (NRCA) Special Inspections
C-NU01
C-NU02
x8 | Non-Residential Certificate Of Installation (NRCI)
| x8s1 | Electrical
|  |  | C-NRCI1 |  | Electric Ready Requirements California Energy Code 2022-CEC-NRCI-ELC-E: https://www.energy.ca.gov/filebrowser/download/5264 |  |  | Responsible Designer Or Installing Contractor
| x8s2 | Envelope
|  |  | C-NRCI2 |  | Envelope Component Approach California Energy Code 2022-CEC-NRCI-ENV-E: https://www.energy.ca.gov/filebrowser/download/5265 |  |  | Responsible Designer Or Installing Contractor
| x8s3 | Lighting
|  |  | C-NRCI3 |  | Indoor Lighting California Energy Code 2022-CEC-NRCI-LTI-E: https://www.energy.ca.gov/filebrowser/download/5266 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCI4 |  | Outdoor Lighting California Energy Code 2022-CEC-NRCI-LTO-E: https://www.energy.ca.gov/filebrowser/download/5267 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCI5 |  | Sign Lighting California Energy Code 2022-CEC-NRCI-LTS-E: https://www.energy.ca.gov/filebrowser/download/5268 |  |  | Responsible Designer Or Installing Contractor
| x8s4 | User Defined Non-Residential Certificate Of Installation (NRCI) Special Inspections
C-NU01
C-NU02
x9 | OTHER
| x9s1 | User Defined Special Inspections
C-OU01
C-OU02
C-OU03
C-OU04
C-OU05
C-OU06
C-OU07
C-OU08
C-OU09
C-OU10
x10 | END OF ON-SITE SPECIAL INSPECTIONS
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F50: Required for projects that use aluminum as a structural material.
Note on F51: Required for projects that include glazing scope that uses structural sealant.
Note on F54: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F55: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F56: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F62: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F63: Required on projects with equipment requiring special seismic certification.
Note on F74: Study required from the Electrical Engineer of Record (EEOR) when new circuit breakers and fuses are installed in new and existing essential electrical systems. Single line diagram and over current protective devices in study shall match approved electrical plans. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F75: Applies to elevator, elevators, dumbwaiters, escalators, moving walks, platform lifts, and stairway chairlifts installations. Study required from the Electrical Engineer of Record (EEOR) when more than one machine is fed from one feeder. Single line diagram and over current protective devices in study shall match approved electrical plans. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F77: Not required for most fire pump installations. Only for new fire pumps in multi-building campus style complexes. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F79: Electrical equipment that is likely to require examination, adjustment, servicing, or maintenance while energized, shall be field or factory marked to warn qualified persons of potential electric arc flash hazards.
Note on F89: For new, remodel, or replacement projects. This type of test is applied to floor, roof, and wall assemblies, and structural members. Consider OPD-0091-13 for Fire-Resistive Standard Details.
Note on F90: Applicable for structural elements on new, remodel, or replacement projects.
Note on F91: For new, remodel, or replacement projects.
Note on F92: For new, remodel, or replacement projects.
Note on F94: For new, remodel, or replacement projects when having erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location. Also prior to occupancy and after sufficient completion for the purposes of pressure-difference testing, flow measurements, and detection and control verification.
Note on F96: For new, remodel, or replacement projects when there is welding sprinkler pipe.
Note on F98: For new, remodel, or replacement projects when standpipe system piping is welded.
Note on F100: For new installations, remodels, replacements or repairs.
Note on F122: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/4927
Note on F123: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/4936
Note on F124: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/4929
Note on F126: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/4940
Note on F128: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/4945
Note on F132: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/4944

## D-Off-Site Special Inspections
|  |  | SECTION D |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | #NAME? |  | #NAME? | #NAME?
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | OFF-SITE SPECIAL INSPECTIONS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Special Inspector) | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
x1 | Structural
| x1s1 | Concrete
|  |  | D-C1 |  | Concrete Mix and Mix Components CBC 1705A.3.3 Batch plant inspection
|  |  | D-C2 |  | Concrete Installation CBC 1705A.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | D-C3 |  | Concrete Mix and Mix Components CBC 1705A.3; ACI-318 26.4.1.5 Admixtures
|  |  | D-C4 |  | Concrete Mix and Mix Components CBC 1705A.3; ACI-318 26.4 Mix design
|  |  | D-C5 |  | Post-Installed and Cast-In Components CBC 1705A.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | D-C6 |  | Post-Installed and Cast-In Components CBC 1705A.3 CIP & post-installed anchors
|  |  | D-C7 |  | Post-Installed and Cast-In Components CBC Table 1705A.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | D-C8 |  | Post-Installed and Cast-In Components CBC 1705A.3; ACI-318 26.13 Specialty inserts, stud rails, rebar mechanical connections, headed rebar
|  |  | D-C9 |  | Prestressed Concrete CBC 1705A.3.4; ACI-318 26.13
|  |  | D-C11 |  | Shotcrete CBC 1705A.3.9 & 1908A Installation
|  |  | D-C12 |  | Insulating Concrete CBC 1705A.3
|  |  | D-C13 |  | Post-Installed and Cast-In Components CBC 1705A.3, 1705A.3.1 & 1903A.8 Welding of reinforcing bars
|  |  | D-C14 |  | GFRC Panels PCI MNL 128 standard
| x1s2 | Masonry
|  |  | D-MA1 |  | Masonry Construction CBC 1705A.4 Laying and grouting
|  |  | D-MA2 |  | Masonry Construction CBC 2104A.1.3 Reinforced grouted masonry
|  |  | D-MA3 |  | Post-Installed and Cast-In Components in Masonry CBC 1705A.4 CIP & post-installed anchors
| x1s3 | Steel
|  |  | D-S1 |  | Fabrication CBC 1705A.2; AISC 360 & AISC 341 Steel shop fabrication
|  |  | D-S2 |  | Welding CBC 1705A.2.1 & 1705A.2.5 Automatic End-Welded Studs
|  |  | D-S3 |  | Welding CBC 1705A.2.5 Weld Inspections
|  |  | D-S4 |  | Welding AWS D1.1 3 & 4, and AWS D1.8 6.1 WPS / WPQR
|  |  | D-S5 |  | High Strength Bolt Installation CBC 1705A.2 & 1705A.2.6
|  |  | D-S6 |  | Cold-Formed Steel Light Frame Construction CBC 1705A.2, 1705A.12.2, & 1705A.13.3
|  |  | D-S7 |  | Special Inspections for Seismic Resistance CBC 1705A.13.1.1 & 1705A.13.1.2 Seismic force-resisting systems and elements
| x1s4 | Wood
|  |  | D-W1 |  | Glue Laminated Timber CBC 1705A.5, 1705A.5.5, & 1705A.12.1
|  |  | D-W2 |  | Timber Connector Installation CBC 1705A.5.6, 1705A.11.1, & 1705A.12.1
|  |  | D-W3 |  | Manufactured Trusses CBC 1705A.5, 1705A.5.2, & 1705A.5.6
|  |  | D-W4 |  | Fastening CBC 1705A.12.1 & 1705A.13.2 Nailing, screw attachment, bolting, anchoring, field gluing operations, and other fastening
| x1s5 | Other Structural Materials
|  |  | D-OM1 |  | Aluminum CBC 2003.1 Inspection
|  |  | D-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 & 1705A.13.5.2 Structural sealants for exterior glass curtain walls
|  |  | D-OM3 |  | Thermal Barriers in Aluminum Mullion Systems CBC 2411.1.2 Testing and inspection
| x1s6 | Alternative Systems
|  |  | D-AS1 |  | Alternative system CBC 1705A.1.1 Construction materials and methods for alternative system
|  |  | D-AS2 |  | Seismic Isolation System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
|  |  | D-AS3 |  | Seismic Damping System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
| x1s7 | Nonstructural components, supports and attachments
|  |  | D-N1 |  | Nonstructural Walls and Components CBC 1705A.13.5 & 1705A.17 Cladding, nonbearing walls, and veneer
|  |  | D-N2 |  | Ceiling CBC 1705A.13.5 Suspended ceiling systems and their anchorage
|  |  | D-N3 |  | Access Floors CBC 1705A.13.5.1 Anchorage of access floor systems
|  |  | D-N4 |  | Storage Racks 8 ft or Taller CBC 1705A.13.7 Anchorage
|  |  | D-N5 |  | Mechanical, Electrical, and Plumbing Components CBC 1705A.13.6 Anchorage, bracing, and vibration isolators
|  |  | D-N6 |  | Special Seismic Certification CBC 1705A.13.4 Special seismic certification label, anchorage, and mounting
| x1s8 | User Defined Structural Special Inspections
D-SU01
D-SU02
x2 | Architectural
| x2s1 | Exterior Finish Systems
|  |  | D-A2 |  | Water-Resistive Barrier Coating CBC 1705A.17.1 ASTM E2570 barrier coating when installed over a sheathing substrate
| x2s2 | Signage
|  |  | D-A4 |  | Accessible Signage CBC 11B-703.1 Visual and tactile requirements
| x2s3 | User Defined Architectural Special Inspections
D-AU01
D-AU02
x3 | Mechanical
| x3s1 | User Defined Mechanical Special Inspections
D-MU01
D-MU02
x4 | Electrical
| x4s1 | User Defined Electrical Special Inspections
D-EU01
D-EU02
x5 | Plumbing
| x5s1 | User Defined Plumbing Special Inspections
D-PU01
D-PU02
x6 | Fire Protection and Life Safety System
| x6s1 | User Defined Fire Protection and Life Safety System Special Inspections
D-FU01
D-FU02
x7 | OTHER
| x7s1 | User Defined Special Inspections
D-OU01
D-OU02
D-OU03
D-OU04
D-OU05
D-OU06
D-OU07
D-OU08
D-OU09
D-OU10
x8 | END OF OFF-SITE SPECIAL INSPECTIONS
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F39: Required for projects that use aluminum as a structural material.
Note on F40: Required for projects that include glazing scope that uses structural sealant.
Note on F43: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F44: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F45: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F51: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F52: Required on projects with equipment requiring special seismic certification.

## E-Required Compliance Forms
SECTION E |  |  | REQUIRED COMPLIANCE FORMS
Facility #: |  | Facility Name: | Project #:
#NAME? |  | #NAME? | #NAME?
Form # | Required (Select with "X") | DOCUMENT NAME | Responsible Designer Or Installing Contractor | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
California Energy Code required compliance forms have been moved to Section C: On-Site Special Inspections
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on D4: Note: Reference numbers will not be sequential once the form is compiled
Note on E4: Place an 'X' in this column to indicate the test is required
Note on F4: Blank rows are provided to add any additional documentation required by local AHJs or other entities specific to the project
Note on G4: Name of the installing contractor which under their purview the items were installed and/or to meet the requirements documented in the NRCC, NRCA and approved construction documents
Note on H4: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted

## F-Cons Verif
SECTION F |  |  |  | CONSTRUCTION VERIFICATION
Facility #: | Facility Name: |  |  | Project #:
#NAME? | #NAME? |  |  | #NAME?
VERIFIED CONSTRUCTION INSPECTION AND OBSERVATION REPORTING
REFERENCE NUMBER |  | PROJECT STAGE(S), MILESTONE, OR INTERVAL (Clearly indicate which Stage(s) apply to which Milestone/Interval) | VERIFIED COMPLIANCE REPORT REQUIRED AS INDICATED (Form HCAI-OSH-123) (See “PERSONAL KNOWLEDGE” as defined in California Administrative Code, Section 7-151) | [8 empty] | HCAI/OSHPD Use (Initial/Date)
|  |  | GEOR | AOR | SEOR | MEOR | EEOR | CONT | IOR | SP INSP | TEST LAB
Clear all plan review Outstanding Items List (OIL) Items
Installation of temporary equipment
Removal of temporary equipment
Substantial Compliance (Remodel, Renovations, Maintenance projects, Equipment Replacement)
Certificate of Occupancy (New Buildings, Additions, Changes in Occupancy)
Construction Final
ACRONYMS: |  | GEOR - Geotechnical Engineer of Record |  | AOR - Architect of Record |  |  |  |  | SEOR - Structural Engineer of Record
|  | MEOR - Mechanical Engineer of Record |  | EEOR - Electrical Engineer of Record |  |  |  |  | CONT O/B - Contractor or Owner/Builder
|  | SP. INSP - Special Inspector |  | IOR - Inspector of Record |  |  |  |  | Test Lab – Engr. For the approved agency
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on F5: Describe each project stage, milestone, or interval for which one or more Verified Compliance Report is required. per CAC 7-141(i) and 7-151(f). A milestone or interval can include multiple stages.
Note on G6: GEOR = Geotechnical Engineer of Record
Note on H6: AOR = Architect or Record (often the Architect in Responsible Charge of the entire project)
Note on I6: SEOR = Structural Engineer of Record
Note on J6: MEOR = Mechanical Engineer of Record
Note on K6: EEOR = Electrical Engineer of Record
Note on L6: CONT = Contractor
Note on M6: IOR = Inspector of Record
Note on N6: SP INSP = Special Inspector Employed by Approved Inspection Agency
Note on O6: TEST LAB = Approved Testing Agency
Note on P6: Additional column may be added here. For large projects attachments may be required to identify all Verified Report Requirements
Note on F23: Aligns with Assembly Bill 2789
Note on F24: Aligns with Assembly Bill 2789

## G-IOR
SECTION G |  | Inspector of Record (IOR) Responsibility
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
INSPECTOR OF RECORD RESPONSIBILITIES. Per CAC 7-145: “The Inspector shall have personal knowledge, obtained by continuous inspection of all work of construction in all stages of its progress to ensure that the work is in accordance with the approved construction documents.” This includes applicable Codes, Referenced Standards, Listings and Manufacturer’s Installation Instructions applicable to the work shown in the approved construction documents. If a project has more than one inspector of record, the distribution of responsibilities for the work shall be clearly identified for each IOR per CAC 7-141(f). One IOR shall be designated as the ‘lead’ IOR per CAC 7-144(b). One IOR shall be assigned responsibility for “all other work” to make sure responsibility for the inspection of every part of the work is assigned.
INSPECTOR OF RECORD CAC 7-141, 7-145 & 7-151 |  | SCOPE OF INSPECTION | PERFORMED OFF-SITE
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## H-Plan Review
SECTION H |  | HCAI REVIEWED
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
NOTE: A structural engineer's signature is required for H and I projects or when they are substantially involved on an S project
Submitted By:
I have reviewed the approved construction documents for this project and all tests and special inspections required by Code are marked as “required” on this form.
Architect/Engineer of Record (Print Name) |  | Professional License # | Architect/Engineer of Record (Signature) | Date
Structural Engineer of Record (Print Name) |  | Professional License # | Structural Engineer of Record (Signature) | Date
FOR HCAI/OSHPD USE
TIO Program Reviewed by HCAI Plan Review Staff:
Note: HCAI plan review staff must provide verification that the TIO program has beeen "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## I-TIO Program Approval
SECTION I |  | TIO PROGRAM APPROVAL
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
This program is prepared and submitted for an OSHPD 1 project. OSHPD 1 projects include all construction and remodel projects for: general acute care hospitals, acute psychiatric hospitals, and general acute care hospitals providing only acute medical rehabilitation center services (CBC 1224.1).
Samples of Test and Special Inspection Reports are NOT required for laboratories approved through OPAA Program
All test and special inspection reports shall be submitted to the IOR, hospital owner, architect in responsible charge, and the structural engineer by the responsible approved agency and/or individual per CAC 7-149(a). The responisble approved agency and/or individual shall be employed by the health facility, owner, or governing board or authority per CAC 7-149(b).
Verified compliance reports shall be signed by the individual who performed the special inspection(s) as outlined in CAC 7-151(a). All reports shall clearly state whether the tests or special inspections were performed in accordance with the HCAI stamped approved documents and whether the results indicate compliance with those documents per CAC 7-149(a). All IORs performing special inspections shall hold the appropriate certification and equipment, and shall obtain approval from the design professional of record and HCAI prior to performing such work.
NOTE: This Test, Inspection, and Observation Report shall be approved by HCAI field personnel prior to start of construction.
Architect/Engineer of Record (Print Name) |  | Professional License # | Architect/Engineer of Record (Signature) | Date
FOR HCAI/OSHPD FIELD STAFF USE
TIO Program Approved by HCAI Field Staff:
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. HCAI Field staff will issue subsequent "TIO Program Approval". If "Approved with Comments" is checked the following comments shall be resolved by the designer prior to proceeding with the related construction:
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## J-Changes
SECTION J |  | CHANGES TO THE TIO PROGRAM
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
Notes: 1) A signature below indicates that the DPOR has verified the acceptance statements in Section I of this Form are applicable to any approved agencies/testing laboratories and special inspectors added. 2) All changes shall be approved as amended construction documents per CAC 7-153, or “concurred with” as non-material alterations per CAC 7-153(b), by HCAI prior to proceeding with the related work. 3) Structural Engineer of Record must only enter initials/date for changes that impact structural.
REVISION NUMBER | SYNOPSIS OF CHANGE | Architect/Engineer of Record (Initial/date) | Structural Engineer of Record (Initial/date) | DATE of Effective Change | HCAI/OSHPD Concurrence (Initial/Date)
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on D5: Enter a Revision Number for each change to the TIO Form
Note on E5: Brief description of the change to the form
Note on F5: Place initials in the box to indicate the architect or engineer in responsible charge has reviewed and approved the changes
Note on G5: Place initials in the box to indicate the structural engineer has reviewed and approved the changes (not required for changes which don't affect structural)
Note on H5: Effective date of the change

## Revision History
Revision number is shown at Section A, bottom right corner.
Version | Date | Description
R26.1 | 2026-01-16 | Revised version number to align with calendar year and month of release.
R26.1 | 2026-01-16 | Moved the Tab E Energy Code Compliance items to Tab C as special inspections. This is to align the spreadsheet version of the TIO with the upcoming eTIO.
R26.1 | 2026-01-16
R26.1 | 2026-01-16 | 2025 CBC: Added B-ME17, B-P22, B-P23, B-P24, B-E16, B-E17, B-E18, B-E19, B-E20, C-E8, C-E9, C-E10, C-E11
R26.1 | 2026-01-16 | 2022 CBC/2025 CBC: Added B-FP26
R26.1 | 2026-01-16 | 2022 CBC/2025 CBC: Removed B-E13, C-E5, C-E7
R26.1 | 2026-01-16 | 2022 CBC/2025 CBC: Moved C-A1 to C-FP8
R26.1 | 2026-01-16 | Added instructions on the "Macro Instructions" tab for when the "Compile error in hidden module" popup displays when opening the spreadsheet.
R26.1.1 | 2026-01-20 | 2022 CBC/2025 CBC: Moved C-A1 to C-FP8
R26.1.1 | 2026-01-20 | 2022 CBC/2025 CBC: Removed cell protections on user defined items
R26.1.2 | 2026-01-20 | 2022 CBC/2025 CBC: Fixed typos in tests and special inspections. Fixed '######' showing over Facility Number on Tab B.