## A-Project Info
Testing, Inspection, and Observation Program
2025 California Building Standards Code OSHPD 2/5
This program is prepared and submitted for an OSHPD 2 or OSHPD 5 project. OSHPD 2 projects are limited to construction and remodel projects for: skilled nursing facilities and/or intermediate-care facilities of Type V, wood or light steel-frame construction (CBC 1225.1). OSHPD 5 projects are limited to construction and remodel projects for: acute psychiatric hospitals subject to licensure (CBC 1228.1).
SECTION A |  | PROJECT INFORMATION
Facility #: | Facility Name: |  | Project #:
Street Address:
City: |  | County:
Record Name (Scope of Project):
Abbreviations:
CAC: California Administrative Code |  | AAMA: American Architectural Manufacturers Association
CBC: California Building Code |  | NFPA: National Fire Protection Association
CEC: California Electrical Code |  | FM: FM Approval Standards
CMC: California Mechanical Code |  | DPOR: Design Professional of Record
CPC: California Plumbing Code
Testing, Inspection, and Observation Stages
Stage No. | Stage Name | Stage Scope / Description
1
DESIGN PROFESSIONAL OF RECORD RESPONSIBILITY
The administration of the work of construction, including this TIO, shall be under the responsible charge of an architect and structural engineer. When a structural engineer is not substantially involved, the architect shall be solely responsible. Where neither structural nor architectural elements are substantially involved, a mechanical or electrical engineer registered in the branch of engineering most applicable to the project may be in responsible charge. (CAC 7-141(a))
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
The "TIO Program Approval" from HCAI field staff must be obtained and included with the notice of start of construction required by CAC Section 7-137(a)4) and 7-145(a)5.A)
Construction shall not commence until the health facility has obtained from HCAI "TIO Program Approval". (CAC Section 7-135(a)3)
Note on I12: Project Number – As assigned by HCAI
Note on G15: Record Name (Scope of Project) – Scope of the project, as shown on the Application for New Project
Note on D23: TIO Stage Description - Provides a name and description/scope for each stage of a TIO program. Select the number of stages for your project by using the list box to the right of the project stage description. If the TIO program will be administered in a single stage then select "1 Stage". The number of stages on Tabs A, B, C, and D will automatically update when the number of stages is selected in the list box.

## B-Tests
|  |  | SECTION B |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | #NAME? |  | #NAME? | #NAME?
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | TESTS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Individual) | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
x1 | Structural
| x1s1 | Foundation
|  |  | B-F1 |  | Soil fill CBC 1705.6 Fill material acceptance test
|  |  | B-F2 |  | Soil fill CBC 1705.6 Compaction test
|  |  | B-F3 |  | Soil and rock anchors CBC 1811 Load test
|  |  | B-F4 |  | Deep foundation elements CBC 1810.3.1.5.1, 1810.3.3.1.2, 1810.3.3.1.5, 1810.3.3.2, & 1810.3.10.4 Load test
|  |  | B-F5 |  | Shoring CBC 1812 Tie-Back Anchors
|  |  | B-F6 |  | Vibro Stone Columns (VSC) CBC 1813 Acceptance Test
|  |  | B-F7 |  | Investigations Required CBC 1803.2 Geotechnical investigation
| x1s2 | Concrete
|  |  | B-C1 |  | Concrete Mix Components CBC 1705.3 & 1910.2.1; ACI 318 1.9.1 & 26.4.1.1 Cementitious materials
|  |  | B-C2 |  | Concrete Mix Components CBC 1705.3; ACI 318 1.9.1 & 26.4.1.2 Aggregates/Reactive aggregates
|  |  | B-C3 |  | Concrete Mix Components CBC 1705.3; ACI 318 26.4.1.4 Water
|  |  | B-C4 |  | Concrete Strength Test CBC 1705.3; ACI 318 26.12 Strength test for concrete and high-strength grout
|  |  | B-C5 |  | Cast-In Components CBC 1705.3 & 1910.2.2; ACI 318 20.2, 25.4.5.1 & 26.6.1.2 Metal reinforcement (including welded wire fabric and headed rebar)
|  |  | B-C6 |  | Cast-In Components CBC 1705.3, 1901.3; ACI 318 20.4 Headed studs and headed stud assemblies
|  |  | B-C7 |  | Cast-In Components CBC Table 1705.3, 1903.5 Weldability of reinforcing bars
|  |  | B-C8 |  | Prestressed Concrete CBC 1705.3 & 1910.2.3; ACI 318 20.3, 25.8 & 26.6.1.2 Prestressing tendons and anchorage
|  |  | B-C9 |  | Strengthening and Repair CBC 1911.2; ACI 548.15 Crack repair by epoxy injection
|  |  | B-C10 |  | Strengthening and Repair CBC 1911.3; ICC-ES AC 178 Sect 9 Strengthening by externally bonded FRP
|  |  | B-C11 |  | Shotcrete CBC 1705.3.9.2 & 1908.1 Preconstruction test
|  |  | B-C12 |  | Shotcrete CBC 1705.3.9 & 1908.1 Strength test
|  |  | B-C13 |  | Post-installed anchors CBC 1901.3.4 Installation verification test (includes adhesive, shot pins and mechanical anchors)
|  |  | B-C14 |  | Existing Post-Installed Anchors CBC 1708 and CAC Ch 6, Sect 11.3 In-situ load tests
| x1s3 | Masonry
|  |  | B-MA1 |  | Mortar and Grout CBC 2105.3 Mortar test
|  |  | B-MA2 |  | Mortar and Grout CBC 2105.3 Grout test
|  |  | B-MA3 |  | Masonry Strength Test CBC 2105.2; TMS 602 1.4.B Compressive strength prism test (f'm)
|  |  | B-MA4 |  | Masonry Strength Test CBC 2105.4 Core tests of masonry wall samples
|  |  | B-MA5 |  | Post-Installed Anchors in Masonry CBC 1705.4 Installation verification test
|  |  | B-MA6 |  | Veneer CBC 1413.2 Veneer bond strength test
|  |  | B-MA7 |  | Architectural Cast Stone CBC 2103.1; ASTM C1354 Strength of stone anchorage
| x1s4 | Steel
|  |  | B-S1 |  | Steel Identification CBC 2201.2 Testing of unidentified steel or identification test for structural steel and cold formed steel
|  |  | B-S2 |  | Steel Components CBC 2216.1 & 1705.2.8 High strength bolts, nuts, and washers
|  |  | B-S3 |  | Steel Components CBC 2216.2 & 1705.2.7 End-welded studs
|  |  | B-S4 |  | Welds CBC 1705.2.7 Nondestructive testing of welds
|  |  | B-S5 |  | Seismic Force Resisting System CBC 2202.4 & 1705.14.1 Nondestructive tests for seismic resistance
| x1s5 | Other Structural Materials
|  |  | B-OM1 |  | Aluminum CBC 2003.1 Testing
|  |  | B-OM2 |  | Structural Sealant Glazing CBC 2410.1.2; AAMA 501.4; AAMA 501.6 Exterior glass curtain walls tests
|  |  | B-OM3 |  | Thermal Barriers in Aluminum Mullion Systems CBC 2411.1.2 Testing of thermal barriers
| x1s6 | Alternative Systems
|  |  | B-AS1 |  | Seismic Isolation System CBC 1705.14.4 Prototype and production test
|  |  | B-AS2 |  | Seismic Damping System CBC 1705.14.4 Prototype and production test
|  |  | B-AS3 |  | Structural Design Criteria CBC 104.2.3 Tests to support alternative system
|  |  | B-AS4 |  | Wind Tunnel Testing CBC 1609.1.1; ASCE 7 31.4 & 31.5; ASCE 49 Wind tunnel testing
| x1s7 | Nonstructural Components, Supports and Attachments
|  |  | B-N1 |  | Special Seismic Certification CBC 1705.14.3 Shake table test
| x1s8 | User Defined Structural Tests
B-SU01
B-SU02
x2 | Architectural
| x2s1 | Radiation Shielding Barriers
|  |  | B-AT1 |  | Radiation Protection CBC 1705.1.1 and 3102C Radiation Shielding Barriers
| x2s2 | Acute Psychiatric Hospital Requirements
|  |  | B-AT2 |  | Doors and Door Openings (OSHPD 5 Only) CBC 1228.4.8 Keyed locks, hinges and door levers
|  |  | B-AT3 |  | Windows and Screens (OSHPD 5 Only) CBC 1228.4.9 Glazing, openings, impact loads, operable windows
|  |  | B-AT4 |  | Ceilings (OSHPD 5 Only) CBC 1228.4.11.4 All M, E, and P shall be concealed
|  |  | B-AT5 |  | Grab Bars (OSHPD 5 Only) CBC 1228.4.18 Anchorage, graspability, and ligature resistant
|  |  | B-AT6 |  | Built-In-Furnishings (OSHPD 5 Only) CBC 1228.4.20 In areas accessible to patients
|  |  | B-AT7 |  | Lighting (OSHPD 5 Only) CBC 1228.4.21.1 Tamper Resistant
|  |  | B-AT8 |  | Handwashing Stations (OSHPD 5 Only) CBC 1228.4.22 Ligature-resistant, laminar flow, goose neck spouts
|  |  | B-AT9 |  | Outdoor Activity Area (OSHPD 5 Only) CBC 1228.13.1.2 Fence doors, gates, lights, cameras, and furniture
| x2s3 | User Defined Architectural Tests
B-AU01
B-AU02
x3 | Mechanical
| x3s1 | Ventilation and Pressurization
|  |  | B-ME1 |  | Listed Hood Assemblies CMC 508.2
|  |  | B-ME2 |  | Type I Hood Capture and Containment Test CMC 511.2.2.2
|  |  | B-ME3 |  | Commercial Kitchen Hood Ventilation CMC 511.2.2.1 Performance test
|  |  | B-ME10 |  | Pre-Demolition Air Balance CMC 407.3.1 Air balance test and report
|  |  | B-ME11 |  | Post-Demolition Air Balance CMC 407.3.1 Air balance test and report
|  |  | B-ME12 |  | Ventilation System Air Balance CMC 407.3.1, Table 4-A Areas tested and balanced
|  |  | B-ME13 |  | Infection Control Planning and Protection ASHRAE 170-2021 5.5 Infection control risk assessment and protection procedure development
|  |  | B-ME14 |  | Duct Leakage Test CMC 603.9.2 SMACNA HVAC air duct leakage test
|  |  | B-ME15 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 416.4 Alarm system test
|  |  | B-ME16 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 417.0 Mechanical system tested and balanced
|  |  | B-ME17 |  | Grease Duct Leakage Test CMC 510.5.3.1 & 510.5.6 Acceptance testing
| x3s2 | Refrigeration Machinery
|  |  | B-ME4 |  | Refrigeration Equipment CMC 1116.2
|  |  | B-ME5 |  | Refrigeration Detection and Alarm System CMC 1106.11.9, 1108.4 & CFC 608.7 Acceptance testing
|  |  | B-ME6 |  | Refrigeration Flaring System CMC 1114.3 Safety and effectiveness
| x3s3 | Boilers/Piping
|  |  | B-ME7 |  | Steam and Hot Water Boilers CMC 1013.0
|  |  | B-ME8 |  | Hydronics CMC 1205.2, 1220.4.6 & 1221.3 Pressure test of steam and water piping
|  |  | B-ME9 |  | Process Piping CMC 1405.2.2 Pressure test
| x3s4 | User Defined Mechanical Tests
B-MU01
B-MU02
x4 | Electrical
| x4s1 | Service and Feeders 1000A or More
|  |  | B-E1 |  | Ground Fault Protection of Equipment CEC 230.95(C) & 517.17(D) Ground Fault performance testing of Service OCPD and all next level feeder OCPD's
| x4s2 | Essential Power Systems
|  |  | B-E2 |  | Emergency Sources and Distribution Equipment CEC 700.3(A), 517.30(B)(5), & NFPA 99 7.13.3 Emergency Systems Commissioning and Acceptance Testing
|  |  | B-E3 |  | Automatic Transfer Switch CEC 517, NFPA 99 7.13.4.3 Testing ATS's for proper operation
|  |  | B-E4 |  | Energy Storage Systems NFPA 111 7.6 Stored-Energy Emergency Power Supply Systems (SEPSS)
|  |  | B-E15 |  | Means of Egress Illumination CBC 1008.2 & 1008.3 Light meter testing of egress lighting
| x4s3 | Patient Care Spaces
|  |  | B-E5 |  | Grounding System in Patient Care Spaces NFPA 99 6.3.3.1 Patient care receptacle testing for proper grounding - Voltage and Impedance testing
|  |  | B-E6 |  | Hospital Grade Receptacles NFPA 99 6.3.3.2.5 Patient care receptacle testing (Polarity and Retention)
| x4s4 | Medium Voltage Systems
|  |  | B-E9 |  | Medium Voltage Outdoor Systems Testing CEC 235.356 Pre-energization and operational tests required for system 100V and more
|  |  | B-E10 |  | Medium Voltage Cable Testing CEC 315.30, 235.356, ANSI/NECA/NCSCB 600, & IEEE 576 Insulation integrity testing required for medium voltage cables.
| x4s5 | Wiring
|  |  | B-E11 |  | Insulation Testing CEC 110.7 Insulation testing of systems less than 1000V
|  |  | B-E12 |  | Torque Electrical Connections CEC 110.3(B) & 110.14(D) Testing/Techniques required to ensure proper torquing of electrical connections
| x4s6 | Low Voltage Systems
|  |  | B-E14 |  | Nurse Call System CEC 517.123 Functional testing of Nurse Call systems
| x4s7 | Power Distribution Systems (<= 1000V)
|  |  | B-E16 |  | Performance Testing Of Arc Energy Reduction Protection System CEC 240.67 Testing of fuses utilized for arc energy reduction
| x4s8 | Power Distribution Systems (< 1000V)
|  |  | B-E17 |  | Performance Testing Of Arc Energy Reduction Protection System CEC 240.87 Testing of circuit breakers utilized for arc energy reduction
| x4s9 | Outdoor Power Distribution Systems (> 1000V)
|  |  | B-E18 |  | Pre-Energization And Acceptance Testing CEC 235.356(A)&(B) Testing of electrical system design including protective relay settings
| x4s10 | Essential Power Sources
|  |  | B-E19 |  | Health Care Microgrid Commissioning CEC 517.30(B)(5) Health Care Microgrids shall be commissioned prior to admitting patients
|  |  | B-E20 |  | On-Site Generators CEC 700.3(A) Health Care Microgrids shall be commissioned prior to admitting patients
| x4s11 | User Defined Electrical Tests
B-EU01
B-EU02
x5 | Plumbing
| x5s1 | Water Supply
|  |  | B-P1 |  | Disinfection of Potable Water Systems CPC 609.10 Disinfection procedures
|  |  | B-P9 |  | Water Supply System CPC 105.3 & 609.4 Pressure tested prior to covering or concealment
|  |  | B-P18 |  | Backflow Prevention Devices and Assemblies CPC 603.2 & 603.4.2 Assembly tested
|  |  | B-P19 |  | Non-Potable Water CPC 1502.0 Testing of alternate water sources and cross-connections
|  |  | B-P20 |  | Recycled Water Supply Systems CPC 1505.6 & 1505.14 Initial cross-connection test and system testing before initial operation
|  |  | B-P21 |  | On-Site Treated Non-Potable Gray Water Systems CPC 1502.1, 1506.6, & 1506.13 Initial cross-connection test and system testing before initial operation
| x5s2 | Medical Gases
|  |  | B-P2 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.10.11.11 Qualification of brazing procedures and brazing
|  |  | B-P3 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.12.2.1 thru 5.1.12.2.7 Installer performed tests |  |  | ASSE 6010 Cert Req'd
|  |  | B-P4 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.12.2.6.7 & 5.1.12.2.7.6 Witness of 24-hour standing pressure test |  |  | ASSE 6020 or 6030 Cert Req'd or Qualified IOR
|  |  | B-P5 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.12.3.1.1 thru 5.1.12.3.1.5 System inspection prior to concealment/cover |  |  | ASSE 6020 or 6030 Cert Req'd
|  |  | B-P6 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.12.3.2.1 Inspection |  |  | ASSE 6020 or 6030 Cert Req'd or Qualified IOR
|  |  | B-P7 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.12.4.2 thru 5.1.12.4.14 System verification |  |  | ASSE 6030 Cert Req'd
|  |  | B-P22 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.12.1.3 Instrument air performance testing
|  |  | B-P23 |  | Medical Gas and Vacuum NFPA 99-2024 Sect 5.1.13.12 Breached systems testing
| x5s3 | Drainage
|  |  | B-P8 |  | Existing Sewers and Drains CPC 102.4.1, 105.3, & 712.0 Tested for conformance with requirements for new work
|  |  | B-P10 |  | Plumbing, Drainage, and Venting Systems CPC 105.3 & 712.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P11 |  | Building Sewer CPC 105.3, 712.0, & 723.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P12 |  | Storm Drain Piping CPC 1107.0 Water or air tested prior to use, covering or concealment
|  |  | B-P14 |  | Private Sewer Disposal System CPC 105.0, & CPC Appendix H H1001.2 Tested prior to use, covering, or concealment
|  |  | B-P16 |  | Defective Systems CPC 105.3.1, 105.3.2, 712.0 Air test of defective drainage and plumbing systems
|  |  | B-P17 |  | Shower Receptors CPC 408.8.5 Leakage test
|  |  | B-P24 |  | Vacuum Drainage Systems CPC 301.3 & C501.8 Vacuum waste system vacuum test
| x5s4 | Fuel Gas
|  |  | B-P13 |  | Fuel Gas Piping CPC 1213.0 & CMC 1313.0 Air, CO2 or nitrogen tested prior to use, covering, or concealment
| x5s5 | Coated Pipe
|  |  | B-P15 |  | Protectively Coated Pipe CPC 312.5 Tested for voids, damage, and imperfections
| x5s6 | User Defined Plumbing Tests
B-PU01
B-PU02
x6 | Fire Protection and Life Safety System
| x6s1 | Fire Alarm
|  |  | B-FP1 |  | Fire Alarm CFC 901.5 & CFC 907.7 NFPA 72-2025 Sect 14.4 Acceptance, testing, and reacceptance testing
| x6s2 | Fire and Smoke Dampers
|  |  | B-FP2 |  | Fire and Smoke Dampers CFC 901.5 & CFC 907.8 Acceptance testing and testing
| x6s3 | Duct Detectors
|  |  | B-FP3 |  | Duct Detectors CFC 901.5, NFPA 72-2025 Sect 14.4 Differential pressure test
| x6s4 | Smoke Control System
|  |  | B-FP4 |  | Smoke Control System CFC 901.5, CFC 909.18 & 1705A.19 Acceptance testing
| x6s5 | Sprinklers
|  |  | B-FP5 |  | Fire Sprinkler CFC 901.5 & NFPA 13-2025 Chapter 29 Above ground piping acceptance testing
|  |  | B-FP6 |  | Fire Sprinkler CFC 901.5 & NFPA 13-2025 Chapter 29 Underground piping acceptance testing
| x6s6 | Standpipe Systems
|  |  | B-FP7 |  | Standpipe Systems CFC 901.5 & NFPA 14-2024 Chapter 11 Above ground piping acceptance testing
|  |  | B-FP8 |  | Standpipe Systems CFC 901.5, CFC 905.3.1 & NFPA 14-2024 Chapter 11 Acceptance testing in buildings 4-stories or more
|  |  | B-FP9 |  | Standpipe Systems CFC 901.5 & NFPA 14-2024 Chapter 11 Underground piping acceptance testing
| x6s7 | Private Fire Mains
|  |  | B-FP10 |  | Private Fire Mains CFC 901.5 & NFPA 24-2025 Sect 10.10 Acceptance testing
| x6s8 | Fire Pumps
|  |  | B-FP11 |  | Fire Pumps CFC 901.5 & NFPA 20-2019 Sect 14.1 & 14.2 Acceptance testing
| x6s9 | Fire Protection Water Tank
|  |  | B-FP12 |  | Fire Protection Water Tank CFC 901.5 & NFPA 22-2018 Chapter 17 Acceptance testing
| x6s10 | Alternative Automatic Fire Extinguishing Systems
|  |  | B-FP13 |  | Wet Chemical Extinguishing System CFC 901.5 & NFPA 17A-2024 Sect 7.4 Acceptance testing
|  |  | B-FP14 |  | Clean Agent Extinguishing System CFC 901.5 & NFPA 2001-2018 Sect 7.7 Acceptance testing
|  |  | B-FP15 |  | CO2 Extinguishing System CFC 901.5 & NFPA 12-2022 Sect 4.4.3 & 4.4.4 Acceptance testing
|  |  | B-FP16 |  | Dry Chemical Extinguishing System CFC 901.5 & NFPA 17-2024 Sect 10.4 Acceptance testing
|  |  | B-FP17 |  | Halon 1301 Extinguishing System CFC 901.5 & NFPA 12A-2022 Sect 6.7 Acceptance testing
| x6s11 | Fuel Tanks
|  |  | B-FP18 |  | Underground Fuel Storage Tank CFC 5704.2.12 & NFPA 30-2024 Sect 21.5.1 Initial testing
|  |  | B-FP19 |  | Underground Fuel Storage Tank CFC 5704.2.12 & NFPA 30-2024 Sect 21.5.2 Tightness testing
|  |  | B-FP20 |  | Flammable and Combustible Liquid Fuel Piping CFC 5703.6.3 Pressure testing
| x6s12 | Emergency Responder Radio Coverage
|  |  | B-FP21 |  | Emergency Responder Radio Coverage CFC 510.5.4 Acceptance test procedure
| x6s13 | Elevators
|  |  | B-FP22 |  | Testing of Elevator Shutdown CBC 3005.5, NFPA 72-2025 21.4, & ASME A17.1/CSA B44-2019
|  |  | B-FP23 |  | Elevator Emergency Operation CBC 3003.2 Emergency recall and in-cart operation
|  |  | B-FP24 |  | Elevator Emergency Standby Power CBC 3003.1 Backup generator engaged
| x6s14 | Fire Door, Fire Shutter, and Fire Windows
|  |  | B-FP25 |  | Fire Door, Fire Shutter, and Fire Windows NFPA 80-2025 5.2 Testing
| x6s15 | Fire Watch
|  |  | B-FP26 |  | Fire Watch CBC 901.7 & CAN 9-901.7 Review of the fire watch log and the written sign off / permission to terminate fire watch.
| x6s16 | User Defined Fire Protection and Life Safety System Tests
B-FU01
B-FU02
x7 | OTHER
| x7s1 | User Defined Tests
B-OU01
B-OU02
B-OU03
B-OU04
B-OU05
B-OU06
B-OU07
B-OU08
B-OU09
B-OU10
x8 | END OF TESTS
Note on F45: Required for projects that use aluminum as a structural material.
Note on F46: Required for projects that include glazing scope that uses structural sealant.
Note on F47: This is for HCAI 1, 1R, 2, 4 & 5. The requirements of this section address the testing and inspection of thermal barriers composite in aluminum mullion systems.
Note on F49: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F50: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F51: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F54: Required on projects where equipment requiring special seismic certification has not been preapproved or justified by analysis.
Note on F60: Required on all projects that contain imaging equipment radiation shielding barriers.
Note on F62: When indicated by the patient Safety Risk Assessment
Note on F63: Windows in patient care areas or areas used by patients
Note on F64: Ceilings shall be monolithic in seclusion rooms, exam/treatment rooms, patient bedrooms, patient toilet rooms, or patient bathing facilities
Note on F65: Grab bars, including those that are part of fixtures such as soap dishes, shall be sufficiently anchored to sustain a concentrated load of 250 pounds (113.4 kg)
Note on F66: Specific requirements for shelves, clothing rods and hooks. Not permitted: doors and drawers, towel bars, shower curtain rods, levers and handles
Note on F67: Lighting in areas identified in the Patient Safety Risk Assessment as high- and medium-risk areas
Note on F68: Handwashing sinks accessible to patients
Note on F69: Specific requirements for fence, gate and door design and installation, lighting, security cameras, and furniture
Note on F75: Listed hood assemblies shall be tested in accordance with UL 710 or equivalent. Listed UV hood assemblies shall be tested in accordance with UL 710 or UL 710C.
Note on F76: Listed hood assemblies shall be tested per manufacturer. Listed UV hoods tested per IAW UL 710 and 710C.
Note on F77: Performance test before final approval of install of ventilation system.
Note on F78: Survey of existing ventilation system priory to start of remodel work.
Note on F79: Survey of ventilation system at completion of remodel work to ensure pre-demolition air balance values are maintained.
Note on F80: Test and balance of new spaces, spaces affected by new equipment or spaces with change in function after completion of work.
Note on F81: For projects that modify or remodel HVAC systems in an existing facility.
Note on F83: Testing of air pressure alarm systems prior to acceptance.
Note on F84: Test and balance of mechanical system after completion of work.
Note on F85: The leakage test shall consist of a light test, water pressure test, or an approved equivalent test.
Note on F87: Factory and field refrigeration system pressure testing.
Note on F88: Alarm system testing of machinery room alarm systems.
Note on F89: Report for approved agency detailing emission products.
Note on F91: Inspection and test protocol for boilers after installation and prior to use.
Note on F92: Pressure testing for system piping and components. Note: piping to be installed in concrete shall be tested per these requirements prior to pouring concrete.
Note on F93: Pressure test at completion of installation.
Note on F99: Ground Gault testing for 480V services and feeders rated 1000A and more. Shall be tested when new services/feeders first installed on site. A written record shall be made available to AHJ. (NOTE: NOT FOR RECEPTACLE GFCI TESTING)
Note on F101: Commissioning for Essential Systems. Commissioning plan should be developed and reviewed before any testing takes place. Testing should demonstrate that the essential electrical sources and distribution systems work effectively to provide essential power to identified loads during a simulated primary site power outage. The AHJ shall be given advance notification at the time at which the acceptance test is to be performed, and the AHJ shall witness the commissioning of the complete system upon installation.
Note on F102: Required testing for new, retrofit and replacement ATSs. Testing should demonstrate that ATS's send signal to start generator upon loss of "normal" power and that power is transferred within code required time limits (Life safety and critical branch within 10 seconds). When normal power is restored the retransfer shall be witnessed for proper operation as part of the commissioning process.
Note on F103: Testing of "large" Battery storage Units used as Emergency Power Supply Systems (SEPSS). The following shall be reviewed by the AHJ 1) Factory test data on the completed system, 2) Battery specifications, 3) Vendor's certificate of compliance to the specifications. (NOTE: A UPS SUPLIED BY AN EMERGENCY POWER SUPPLY SYSTEM IS NOT REQUIRED TO BE TESTED TO NFPA 111).
Note on F104: Egress lighting levels should be checked with a light meter prior to granting occupancy.
Note on F106: For new construction the effectiveness of the grounding system for receptacles shall be evaluated before acceptance. Voltage and impedance measurements are required to test the effectiveness of the grounding system in Patient Care spaces (like head walls). Voltage limit is 20 mV, impedance limit 0.1 ohms if standard receptacles, or 0.2 ohms if isolated ground receptacles. 10% of receptacles shall be tested (both normal and essential power receptacles and at least one receptacle tested in each patient care space.
Note on F107: Testing required for all receptacles in patient care spaces is required after installation or replacement of devices and prior to putting in service. Correct polarity and receptacle retention force shall be tested for all receptacles. Retention force shall not be less than 115 g (4 oz).
Note on F109: Medium voltage (over 1000 Volts) system testing. Might be provided for a large hospital campus'. Pre-energization and operational tests are required for new and modified electrical systems over 1000V.
Note on F110: Testing of new medium volt cables (over 1000 Volts). Related to Medium Voltage Outdoor Systems - Inspections and Test. Meggar testing and ULF testing are both acceptable
Note on F112: Megger test of new conductors (208Y/120V & 480Y/277V) to ensure wiring is free from short circuits and ground faults.
Note on F113: For panelboards, switchboards, switchgear, MCC, devices and other electrical equipment that require electrical connections to be torqued per manufacture instructions.
Note on F115: Functional testing of new or modified nurse call systems. This is a functional test required to demonstrate that the nurse call system functions meet code requirements.
Note on F117: Performance testing of fuses. The arc energy reduction protection system shall be performance tested by primary current injection testing or another approved method when first installed on site. This testing shall be conducted by a qualified person(s) in accordance with the manufacturer's instructions. A written record of this testing shall be made and shall be available to the authority having jurisdiction.
Note on F119: Performance testing of circuit breakers. The arc energy reduction protection system shall be performance tested by primary current injection testing or another approved method when first installed on site. This testing shall be conducted by a qualified person(s) in accordance with the manufacturer's instructions. A written record of this testing shall be made and shall be available to the authority having jurisdiction.
Note on F121: Pre-energization and acceptance testing systems over 1000V. The complete electrical system design, including setting for protective, switching and control circuits, shall be performance tested and made available to the AHJ. Each protective switching and control circuit shall be adjusted in accordance with the system design and tested by actual operation using current injection or equivalent methods as necessary A test report covering the results of the test required in CEC 235.356(A) shall be delivered to the AHJ prior to energization of the equipment.
Note on F123: Health Care Microgrids shall meet the commissioning requirements called out in NFPA 99 Section 6.10.7
Note on F124: Permanently installed on-site (emergency) generator sets for Health Care Facilities shall be commissioned in the presence of OSHPD personnel and tested in accordance with NFPA 110 section 7.1.3
Note on F130: Testing to be done for new piping and when pipes have been breached in project. Not for fixture replacement.
Note on F131: Testing of completion of new segment or entire system.
Note on F132: Device shall be approved by the AHJ and then tested at time of installation, repair, or relocation.
Note on F133: Testing of all new alternate water sources for non-potable water including testing emphasis on cross-connection prevention.
Note on F137: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F138: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F139: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F140: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F141: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F142: Verification tests shall be performed only after all installer performed tests have been completed.
Note on F143: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F144: All systems that are breached and all components that are subject to additions, renovations, or replacement shall be inspected and tested.
Note on F146: Testing for modified or breached sewer piping.
Note on F147: Testing of completion of new segment or entire system.
Note on F148: Testing of completion of new segment or entire system.
Note on F149: Water or air testing for new storm drain piping, and parts of existing storm drain piping that have been altered, extended, or repaired.
Note on F150: Static and fluid water testing after installation.
Note on F151: Air testing of existing drainage or plumbing that is suspected to be defective.
Note on F152: Standing water test for drain/receptor interface.
Note on F153: Testing shall be performed on all new vacuum waste piping.
Note on F155: Testing required for new, or repaired fuel piping prior to acceptance and initial operation.
Note on F163: For new installations, remodels, replacements or repairs. When required, test when interconnected with other systems. and before the occupancy of the building or specific area.
Note on F165: Shall be tested when the system is altered or modified. When required, test when interconnected with other systems.
Note on F167: For new installations, remodels, replacements, repairs, or when there are changes to the site-specific software. When required, test when interconnected with other systems. Shall notify HCAI and owner prior to initial acceptance test.
Note on F169: For new installations, remodels, replacements or repairs. When required, test when interconnected with other systems. Test shall include function, sequence and, where applicable, capacity of their installed condition. Test shall be prior to concealment and prior to occupancy.
Note on F171: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F172: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F174: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independently. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F175: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independently. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F176: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independently. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F178: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F180: For new installations, remodels, replacements or repairs. If components that affect performance are replaced, then a retest shall be conducted by the pump manufacturer or designated representative or qualified persons acceptable to HCAI.
Note on F182: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test. Prior to placing the tank in service, a representative of the tank contractor and a representative of the owner shall conduct a joint inspection of the completed equipment.
Note on F184: For new installations, remodels, replacements or repairs.
Note on F185: For new installations, remodels, replacements or repairs.
Note on F186: For new installations, remodels, replacements or repairs.
Note on F187: For new installations, remodels, replacements or repairs.
Note on F188: For new installations, remodels, replacements or repairs.
Note on F190: For new installations, remodels, replacements or repairs.
Note on F191: For new installations, remodels, replacements or repairs.
Note on F192: For new installations, remodels, replacements or repairs.
Note on F194: For new installations, remodels, replacements or repairs.
Note on F196: For new installations, remodels, replacements or repairs.
Note on F197: For new installations, remodels, replacements or repairs.
Note on F198: For new installations, remodels, replacements or repairs.
Note on F200: For new installations, remodels, replacements or repairs.

## C-On-Site Special Inspections
|  |  | SECTION C |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | #NAME? |  | #NAME? | #NAME?
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | ON-SITE SPECIAL INSPECTIONS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Special Inspector) | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
x1 | Structural
| x1s1 | Foundation
|  |  | C-F1 |  | Soils CBC 1705.6 Soil fill
|  |  | C-F2 |  | Soils CBC 1705.6 Bearing capacity of materials below shallow foundations
|  |  | C-F3 |  | Soils CBC 1705.6 Excavation depth
|  |  | C-F4 |  | Deep Foundations CBC 1705.7 Driven deep foundations
|  |  | C-F5 |  | Deep Foundations CBC 1705.8 Cast-in-place deep foundations
|  |  | C-F6 |  | Deep Foundations CBC 1705.9 Helical pile foundations
|  |  | C-F7 |  | Shoring CBC 1812 Shoring
|  |  | C-F8 |  | Vibro Stone Columns (VSC) CBC 1813 Vibro stone columns
|  |  | C-F9 |  | Prestressed Soil and Rock Anchors CBC 1811 & 1812 Installation and testing
| x1s2 | Concrete
|  |  | C-C2 |  | Concrete Installation CBC 1705.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | C-C3 |  | Concrete Mix and Mix Components CBC 1705.3; ACI-318 26.4.1.5 Admixtures
|  |  | C-C4 |  | Concrete Mix and Mix Components CBC 1705.3; ACI-318 26.4 Mix design
|  |  | C-C5 |  | Post-Installed and Cast-In Components CBC 1705.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | C-C6 |  | Post-Installed and Cast-In Components CBC 1705.3 CIP & post-installed anchors
|  |  | C-C7 |  | Post-Installed and Cast-In Components CBC Table 1705.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | C-C8 |  | Post-Installed and Cast-In Components CBC 1705.3; ACI-318 26.13 Specialty inserts, stud rails, rebar mechanical connections, headed rebar
|  |  | C-C9 |  | Prestressed Concrete CBC 1705.3.4; ACI-318 26.13
|  |  | C-C10 |  | Precast Concrete Erection CBC 1705.3; ACI 318 26.9, 26.13.1 & 26.13.3.3
|  |  | C-C11 |  | Shotcrete CBC 1705.3.9 & 1908 Installation
|  |  | C-C12 |  | Insulating Concrete CBC 1705.3
|  |  | C-C13 |  | Post-Installed and Cast-In Components CBC 1705.3, 1705.3.1 & 1903.5 Welding of reinforcing bars
|  |  | C-C14 |  | GFRC Panels PCI MNL 128 standard
|  |  | C-C15 |  | Strengthening and Repair CBC 1911.2; ACI 548.15 Crack repair by epoxy injection
|  |  | C-C16 |  | Strengthening and Repair CBC 1911.3; ICC AC178 Sect 3 to 8 Strengthening by externally bonded FRP
| x1s3 | Masonry
|  |  | C-MA1 |  | Masonry Construction CBC 1705.4 Laying and grouting
|  |  | C-MA2 |  | Masonry Construction CBC 2104.2 Reinforced grouted masonry
|  |  | C-MA3 |  | Post-Installed and Cast-In Components in Masonry CBC 1705.4 CIP & post-installed anchors
| x1s4 | Steel
|  |  | C-S2 |  | Welding CBC 1705.2.1 & 1705.2.7 Automatic End-Welded Studs
|  |  | C-S3 |  | Welding CBC 1705.2.7 Weld Inspections
|  |  | C-S4 |  | Welding AWS D1.1 5 & 6, and AWS D1.8 7 WPS / WPQR
|  |  | C-S5 |  | High Strength Bolt Installation CBC 1705.2 & 1705.2.8
|  |  | C-S6 |  | Cold-Formed Steel Light Frame Construction CBC 1705.2.9, 1705.12.2, & 1705.13.3
|  |  | C-S7 |  | Special Inspections for Seismic Resistance CBC 1705.13.1.1 & 1705.13.1.2 Seismic force-resisting systems and elements
| x1s5 | Wood
|  |  | C-W1 |  | Glue Laminated Timber CBC 1705.5, 1705.5.5, & 1705.12.1
|  |  | C-W2 |  | Timber Connector Installation CBC 1705.5.7, 1705.12.1, & 1705.13.2
|  |  | C-W3 |  | Manufactured Trusses CBC 1705.5, 1705.5.2, 1705.5.4, & 1705.5.6
|  |  | C-W4 |  | Fastening CBC 1705.12.1 & 1705.13.2 Nailing, screw attachment, bolting, anchoring, field gluing operations, and other fastening
| x1s6 | Other Structural Materials
|  |  | C-OM1 |  | Aluminum CBC 2003.1 Inspection
|  |  | C-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 Structural sealants for exterior glass curtain walls
|  |  | C-OM3 |  | Thermal Barriers in Aluminum Mullion Systems CBC 2411.1.2 Testing and inspection
| x1s7 | Alternative Systems
|  |  | C-AS1 |  | Alternative system CBC 1705.1.1 Construction materials and methods for alternative system
|  |  | C-AS2 |  | Seismic Isolation System CBC 1705.13.8 Fabrication, installation, prototype, and production testing
|  |  | C-AS3 |  | Seismic Damping System CBC 1705.13.8 Fabrication, installation, prototype, and production testing
| x1s8 | Nonstructural components, supports and attachments
|  |  | C-N1 |  | Nonstructural Walls and Components CBC 1705.13.5 & 1705.17 Cladding, nonbearing walls, and veneer
|  |  | C-N2 |  | Ceiling CBC 1705.13.5 Suspended ceiling systems and their anchorage
|  |  | C-N3 |  | Access Floors CBC 1705.13.5.1 Anchorage of access floor systems
|  |  | C-N4 |  | Storage Racks 8 ft or Taller CBC 1705.13.7 Anchorage
|  |  | C-N5 |  | Mechanical, Electrical, and Plumbing Components CBC 1705.13.6 Anchorage, bracing, and vibration isolators
|  |  | C-N6 |  | Special Seismic Certification CBC 1705.13.4 Special seismic certification label, anchorage, and mounting
| x1s9 | User Defined Structural Special Inspections
C-SU01
C-SU02
x2 | Mechanical
| x2s1 | User Defined Mechanical Special Inspections
C-MU01
C-MU02
x3 | Electrical
| x3s1 | Electrical Equipment
|  |  | C-E1 |  | Equipment rated for 1000A or more CEC 110.16(B) Arc Flash Labels
|  |  | C-E8 |  | Industrial Control Panels CEC 409.110 Industrial control panel markings
|  |  | C-E9 |  | Electrical Motor Control Centers (MCCs) CEC 430.98 Motor control center bus rating and short circuiting rating
|  |  | C-E10 |  | Elevator Electrical Disconnects CEC 620.51(D) Available fault current ratings
| x3s2 | Adjustable Overcurrent Protection Devices
|  |  | C-E2 |  | Essential power OCPDs CEC 517.31(G) Manufacturer, model number, and adjustable settings shall match the coordination study.
|  |  | C-E3 |  | Elevator OCPDs CEC 620.62 Manufacturer, model number, and adjustable settings shall match the coordination study.
|  |  | C-E4 |  | Fire Pump OCPDs CEC 695.3(C)(3) Manufacturer, model number, and adjustable settings shall match the coordination study.
| x3s3 | Labeling
|  |  | C-E6 |  | Arc Flash Hazard Warning CEC 110.16(A) Switchboards, switchgear, panel boards, industrial control panels, and motor control centers shall have arc flash labels.
| x3s4 | Service Entrance Equipment
|  |  | C-E11 |  | Emergency Power Sources CEC 700.5(E) Service equipment signage to indicate emergency power sources
| x3s5 | User Defined Electrical Special Inspections
C-EU01
C-EU02
x4 | Plumbing
| x4s1 | User Defined Plumbing Special Inspections
C-PU01
C-PU02
x5 | Fire Protection and Life Safety System
| x5s1 | Fireproofing and Fire Stopping
|  |  | C-FP1 |  | Sprayed Fire-Resistive Materials CBC 1705.15 Spray-applied fireproofing
|  |  | C-FP2 |  | Mastic and Intumescent Fire-Resistive Materials CBC 1705.16 In accordance with AWCI 12-B
|  |  | C-FP3 |  | Penetration Firestops CBC 1705.18.1 Penetration firestop systems that are tested and listed
|  |  | C-FP4 |  | Fire-Resistant Joint Systems CBC 1705.18.2 Fire-resistant joint systems that are tested and listed
| x5s2 | Smoke Control Systems
|  |  | C-FP5 |  | Smoke Control Systems CFC 909.18.8, CBC 1705.14.3.1, & 1705.19 Ductwork and operation
| x5s3 | Sprinklers
|  |  | C-FP6 |  | Sprinkler System Piping NFPA 13-2025 Sect 7.5.2 Welded pipe and fittings
| x5s4 | Standpipe Systems
|  |  | C-FP7 |  | Standpipe System Piping NFPA 14-2024 Sect 4.4.2 Welded pipe and fittings
| x5s5 | Exterior Finish Systems
|  |  | C-FP8 |  | Exterior insulation and finish systems (EIFS) CBC 1705.17 EIFS applications
| x5s6 | User Defined Fire Protection and Life Safety System Special Inspections
C-FU01
C-FU02
x6 | Architectural
| x6s1 | Exterior Finish Systems
|  |  | C-A2 |  | Water-Resistive Barrier Coating CBC 1705.17.1 ASTM E2570 barrier coating when installed over a sheathing substrate
| x6s2 | Signage
|  |  | C-A3 |  | Exit Signs CBC 1013.1 Location, illumination and physical characteristics
|  |  | C-A4 |  | Accessible Signage CBC 11B-703.1 Visual and tactile requirements
| x6s3 | Roof Coverings
|  |  | C-A5 |  | Substrate for Roof Coverings CBC 1507 Requirements for Roof Coverings
|  |  | C-A6 |  | Installation of Roof Coverings CBC 1506 Materials
| x6s4 | User Defined Architectural Special Inspections
C-AU01
C-AU02
x7 | Non-Residential Certificate Of Acceptance (NRCA)
| x7s1 | Covered Processes
|  |  | C-NRCA1 |  | Compressed Air System Controls (3 or more compressors and greater than 100hp) California Energy Code NRCA-PRC-01a-F: https://www.energy.ca.gov/filebrowser/download/8536 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA2 |  | Compressed Air System Controls (2 or less compressors and 100hp or greater) California Energy Code NRCA-PRC-01b-F: https://www.energy.ca.gov/filebrowser/download/8537 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA3 |  | Parking Garage Ventilation California Energy Code NRCA-PRC-03-F: https://www.energy.ca.gov/filebrowser/download/8539 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA4 |  | Escalator and Moving Walkway Speed Control California Energy Code NRCA-PRC-13-F: https://www.energy.ca.gov/filebrowser/download/8546 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA5 |  | Steam Traps Fault - Summary California Energy Code NRCA-PRC-18a-F: https://www.energy.ca.gov/filebrowser/download/8555 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA6 |  | Steam Traps Fault - Individual California Energy Code NRCA-PRC-18b-F: https://www.energy.ca.gov/filebrowser/download/8468 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA7 |  | Steam Traps Fault - Group California Energy Code NRCA-PRC-18c-F: https://www.energy.ca.gov/filebrowser/download/8469 |  |  | Responsible Designer Or Installing Contractor
| x7s2 | Envelope
|  |  | C-NRCA8 |  | Fenestration Acceptance California Energy Code NRCA-ENV-02-F: https://www.energy.ca.gov/filebrowser/download/8476 |  |  | Responsible Designer Or Installing Contractor
| x7s3 | Lighting
|  |  | C-NRCA9 |  | Outdoor Lighting Controls California Energy Code NRCA-LTO-02-A: https://www.energy.ca.gov/filebrowser/download/8485 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA10 |  | Shut-Off Lighting Controls California Energy Code NRCA-LTI-02-A: https://www.energy.ca.gov/filebrowser/download/8697 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA11 |  | Daylighting Responsive Controls California Energy Code NRCA-LTI-03-A: https://www.energy.ca.gov/filebrowser/download/8482 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCA12 |  | Institutional Tuning Power Adjustment Factor (PAF) California Energy Code NRCA-LTI-05-A: https://www.energy.ca.gov/filebrowser/download/8484 |  |  | Responsible Designer Or Installing Contractor
| x7s4 | User Defined Non-Residential Certificate Of Acceptance (NRCA) Special Inspections
C-NU01
C-NU02
x8 | Non-Residential Certificate Of Installation (NRCI)
| x8s1 | Electrical
|  |  | C-NRCI1 |  | Electrical Power Distribution California Energy Code NRCI-ELC-E: https://www.energy.ca.gov/filebrowser/download/8474 |  |  | Responsible Designer Or Installing Contractor
| x8s2 | Envelope
|  |  | C-NRCI2 |  | Envelope Component Approach California Energy Code NRCI-ENV-E: https://www.energy.ca.gov/filebrowser/download/8479 |  |  | Responsible Designer Or Installing Contractor
| x8s3 | Lighting
|  |  | C-NRCI3 |  | Indoor Lighting - Prescriptive California Energy Code NRCI-LTI-E: https://www.energy.ca.gov/filebrowser/download/8489 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCI4 |  | Outdoor Lighting California Energy Code NRCI-LTO-E: https://www.energy.ca.gov/filebrowser/download/8490 |  |  | Responsible Designer Or Installing Contractor
|  |  | C-NRCI5 |  | Sign Lighting California Energy Code NRCI-LTS-E: https://www.energy.ca.gov/filebrowser/download/8491 |  |  | Responsible Designer Or Installing Contractor
| x8s4 | User Defined Non-Residential Certificate Of Installation (NRCI) Special Inspections
C-NU01
C-NU02
x9 | OTHER
| x9s1 | User Defined Special Inspections
C-OU01
C-OU02
C-OU03
C-OU04
C-OU05
C-OU06
C-OU07
C-OU08
C-OU09
C-OU10
x10 | END OF ON-SITE SPECIAL INSPECTIONS
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F50: Required for projects that use aluminum as a structural material.
Note on F51: Required for projects that include glazing scope that uses structural sealant.
Note on F54: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F55: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F56: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F62: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F63: Required on projects with equipment requiring special seismic certification.
Note on F73: Arc flash label with date of calculations are required on service equipment and feeder supplied equipment rated over 1000A.
Note on F74: Industrial control panels shall have permanent markings to show the manufacturers name, supply voltage, number of phases, frequency and full load current, short circuit rating, electrical wiring diagram, and an enclosure type number .
Note on F75: Motor control centers shall be permanently marked with bus rating and MCC short circuit rating.
Note on F76: Elevator disconnect means shall be legibly marked in the field with the available fault current. Marking shall include the date the available fault current calculation was provided.
Note on F79: Required for single source that feeds multiple elevators.
Note on F80: Only required if multi-building complex with medium voltage distribution.
Note on F82: Electrical equipment that is likely to require examination, adjustment, servicing, or maintenance while energized, shall be field or factory marked to warn qualified persons of potential electric arc flash hazards.
Note on F84: A sign shall be placed at the service entrance equipment indicating the type and location of each on-site emergency power source.
Note on F94: For new, remodel, or replacement projects. This type of test is applied to floor, roof, and wall assemblies, and structural members. Consider OPD-0091-13 for Fire-Resistive Standard Details.
Note on F95: Applicable for structural elements on new, remodel, or replacement projects.
Note on F96: For new, remodel, or replacement projects.
Note on F97: For new, remodel, or replacement projects.
Note on F99: For new, remodel, or replacement projects when having erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location. Also prior to occupancy and after sufficient completion for the purposes of pressure-difference testing, flow measurements, and detection and control verification.
Note on F101: For new, remodel, or replacement projects when there is welding sprinkler pipe.
Note on F103: For new, remodel, or replacement projects when standpipe system piping is welded.
Note on F123: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8868
Note on F124: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8868
Note on F125: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8870
Note on F126: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8877
Note on F129: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8882
Note on F131: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8883
Note on F133: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8890
Note on F134: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8885
Note on F135: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8887
Note on F136: Click for Additional Information: https://www.energy.ca.gov/filebrowser/download/8917

## D-Off-Site Special Inspections
|  |  | SECTION D |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | #NAME? |  | #NAME? | #NAME?
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | OFF-SITE SPECIAL INSPECTIONS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Special Inspector) | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
x1 | Structural
| x1s1 | Concrete
|  |  | D-C1 |  | Concrete Mix and Mix Components CBC 1705.3.3 Batch plant inspection
|  |  | D-C2 |  | Concrete Installation CBC 1705.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | D-C3 |  | Concrete Mix and Mix Components CBC 1705.3; ACI-318 26.4.1.5 Admixtures
|  |  | D-C4 |  | Concrete Mix and Mix Components CBC 1705.3; ACI-318 26.4 Mix design
|  |  | D-C5 |  | Post-Installed and Cast-In Components CBC 1705.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | D-C6 |  | Post-Installed and Cast-In Components CBC 1705.3 CIP & post-installed anchors
|  |  | D-C7 |  | Post-Installed and Cast-In Components CBC Table 1705.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | D-C8 |  | Post-Installed and Cast-In Components CBC 1705.3; ACI-318 26.13 Specialty inserts, stud rails, rebar mechanical connections, headed rebar
|  |  | D-C9 |  | Prestressed Concrete CBC 1705.3.4; ACI-318 26.13
|  |  | D-C11 |  | Shotcrete CBC 1705.3.9 & 1908 Installation
|  |  | D-C12 |  | Insulating Concrete CBC 1705.3
|  |  | D-C13 |  | Post-Installed and Cast-In Components CBC 1705.3, 1705.3.1 & 1903.5 Welding of reinforcing bars
|  |  | D-C14 |  | GFRC Panels PCI MNL 128 standard
| x1s2 | Masonry
|  |  | D-MA1 |  | Masonry Construction CBC 1705.4 Laying and grouting
|  |  | D-MA2 |  | Masonry Construction CBC 2104.2 Reinforced grouted masonry
|  |  | D-MA3 |  | Post-Installed and Cast-In Components in Masonry CBC 1705.4 CIP & post-installed anchors
| x1s3 | Steel
|  |  | D-S1 |  | Fabrication CBC 1705.2; AISC-360; AISC-341 Steel shop fabrication
|  |  | D-S2 |  | Welding CBC 1705.2.1 & 1705.2.7 Automatic End-Welded Studs
|  |  | D-S3 |  | Welding CBC 1705.2.7 Weld Inspections
|  |  | D-S4 |  | Welding AWS D1.1 5 & 6, and AWS D1.8 7 WPS / WPQR
|  |  | D-S5 |  | High Strength Bolt Installation CBC 1705.2 & 1705.2.8
|  |  | D-S6 |  | Cold-Formed Steel Light Frame Construction CBC 1705.2.9, 1705.12.2, & 1705.13.3
|  |  | D-S7 |  | Special Inspections for Seismic Resistance CBC 1705.13.1.1 & 1705.13.1.2 Seismic force-resisting systems and elements
| x1s4 | Wood
|  |  | D-W1 |  | Glue Laminated Timber CBC 1705.5, 1705.5.5, & 1705.12.1
|  |  | D-W2 |  | Timber Connector Installation CBC 1705.5.7, 1705.12.1, & 1705.13.2
|  |  | D-W3 |  | Manufactured Trusses CBC 1705.5, 1705.5.2, 1705.5.4, & 1705.5.6
|  |  | D-W4 |  | Fastening CBC 1705.12.1 & 1705.13.2 Nailing, screw attachment, bolting, anchoring, field gluing operations, and other fastening
| x1s5 | Other Structural Materials
|  |  | D-OM1 |  | Aluminum CBC 2003.1 Inspection
|  |  | D-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 Structural sealants for exterior glass curtain walls
|  |  | D-OM3 |  | Thermal Barriers in Aluminum Mullion Systems CBC 2411.1.2 Testing and inspection
| x1s6 | Alternative Systems
|  |  | D-AS1 |  | Alternative system CBC 1705.1.1 Construction materials and methods for alternative system
|  |  | D-AS2 |  | Seismic Isolation System CBC 1705.13.8 Fabrication, installation, prototype, and production testing
|  |  | D-AS3 |  | Seismic Damping System CBC 1705.13.8 Fabrication, installation, prototype, and production testing
| x1s7 | Nonstructural components, supports and attachments
|  |  | D-N1 |  | Nonstructural Walls and Components CBC 1705.13.5 & 1705.17 Cladding, nonbearing walls, and veneer
|  |  | D-N2 |  | Ceiling CBC 1705.13.5 Suspended ceiling systems and their anchorage
|  |  | D-N3 |  | Access Floors CBC 1705.13.5.1 Anchorage of access floor systems
|  |  | D-N4 |  | Storage Racks 8 ft or Taller CBC 1705.13.7 Anchorage
|  |  | D-N5 |  | Mechanical, Electrical, and Plumbing Components CBC 1705.13.6 Anchorage, bracing, and vibration isolators
|  |  | D-N6 |  | Special Seismic Certification CBC 1705.13.4 Special seismic certification label, anchorage, and mounting
| x1s8 | User Defined Structural Special Inspections
D-SU01
D-SU02
x2 | Architectural
| x2s1 | Exterior Finish Systems
|  |  | D-A2 |  | Water-Resistive Barrier Coating CBC 1705.17.1 ASTM E2570 barrier coating when installed over a sheathing substrate
| x2s2 | Signage
|  |  | D-A4 |  | Accessible Signage CBC 11B-703.1 Visual and tactile requirements
| x2s3 | User Defined Architectural Special Inspections
D-AU01
D-AU02
x3 | Mechanical
| x3s1 | User Defined Mechanical Special Inspections
D-MU01
D-MU02
x4 | Electrical
| x4s1 | User Defined Electrical Special Inspections
D-EU01
D-EU02
x5 | Plumbing
| x5s1 | User Defined Plumbing Special Inspections
D-PU01
D-PU02
x6 | Fire Protection and Life Safety System
| x6s1 | User Defined Fire Protection and Life Safety System Special Inspections
D-FU01
D-FU02
x7 | OTHER
| x7s1 | User Defined Special Inspections
D-OU01
D-OU02
D-OU03
D-OU04
D-OU05
D-OU06
D-OU07
D-OU08
D-OU09
D-OU10
x8 | END OF OFF-SITE SPECIAL INSPECTIONS
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F39: Required for projects that use aluminum as a structural material.
Note on F40: Required for projects that include glazing scope that uses structural sealant.
Note on F43: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F44: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F45: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F51: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F52: Required on projects with equipment requiring special seismic certification.

## E-Required Compliance Forms
SECTION E |  |  | REQUIRED COMPLIANCE FORMS
Facility #: |  | Facility Name: | Project #:
#NAME? |  | #NAME? | #NAME?
Form # | Required (Select with "X") | DOCUMENT NAME | Responsible Designer Or Installing Contractor | Compliance Verification by IOR (Initial/Date) | HCAI/OSHPD Use (Initial/Date)
California Energy Code required compliance forms have been moved to Section C: On-Site Special Inspections
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on D4: Note: Reference numbers will not be sequential once the form is compiled
Note on E4: Place an 'X' in this column to indicate the test is required
Note on F4: Blank rows are provided to add any additional documentation required by local AHJs or other entities specific to the project
Note on G4: Name of the installing contractor which under their purview the items were installed and/or to meet the requirements documented in the NRCC, NRCA and approved construction documents
Note on H4: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted

## F-Cons Verif
SECTION F |  |  |  | CONSTRUCTION VERIFICATION
Facility #: | Facility Name: |  |  | Project #:
#NAME? | #NAME? |  |  | #NAME?
VERIFIED CONSTRUCTION INSPECTION AND OBSERVATION REPORTING
REFERENCE NUMBER |  | PROJECT STAGE(S), MILESTONE, OR INTERVAL (Clearly indicate which Stage(s) apply to which Milestone/Interval) | VERIFIED COMPLIANCE REPORT REQUIRED AS INDICATED (Form HCAI-OSH-123) (See “PERSONAL KNOWLEDGE” as defined in California Administrative Code, Section 7-151) | [8 empty] | HCAI/OSHPD Use (Initial/Date)
|  |  | GEOR | AOR | SEOR | MEOR | EEOR | CONT | IOR | SP INSP | TEST LAB
Clear all plan review Outstanding Items List (OIL) Items
Installation of temporary equipment
Removal of temporary equipment
Substantial Compliance (Remodel, Renovations, Maintenance projects, Equipment Replacement)
Certificate of Occupancy (New Buildings, Additions, Changes in Occupancy)
Construction Final
ACRONYMS: |  | GEOR - Geotechnical Engineer of Record |  | AOR - Architect of Record |  |  |  |  | SEOR - Structural Engineer of Record
|  | MEOR - Mechanical Engineer of Record |  | EEOR - Electrical Engineer of Record |  |  |  |  | CONT O/B - Contractor or Owner/Builder
|  | SP. INSP - Special Inspector |  | IOR - Inspector of Record |  |  |  |  | Test Lab - Engr. For the approved agency
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on F5: Describe each project stage, milestone, or interval for which one or more Verified Compliance Report is required. per CAC 7-141(i) and 7-151(f). A milestone or interval can include multiple stages.
Note on G6: GEOR = Geotechnical Engineer of Record
Note on H6: AOR = Architect or Record (often the Architect in Responsible Charge of the entire project)
Note on I6: SEOR = Structural Engineer of Record
Note on J6: MEOR = Mechanical Engineer of Record
Note on K6: EEOR = Electrical Engineer of Record
Note on L6: CONT = Contractor
Note on M6: IOR = Inspector of Record
Note on N6: SP INSP = Special Inspector Employed by Approved Inspection Agency
Note on O6: TEST LAB = Approved Testing Agency
Note on P6: Additional column may be added here. For large projects attachments may be required to identify all Verified Report Requirements
Note on F23: Aligns with Assembly Bill 2789
Note on F24: Aligns with Assembly Bill 2789

## G-IOR
SECTION G |  | Inspector of Record (IOR) Responsibility
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
INSPECTOR OF RECORD RESPONSIBILITIES. Per CAC 7-145: “The Inspector shall have personal knowledge, obtained by continuous inspection of all work of construction in all stages of its progress to ensure that the work is in accordance with the approved construction documents.” This includes applicable Codes, Referenced Standards, Listings and Manufacturer's Installation Instructions applicable to the work shown in the approved construction documents. If a project has more than one inspector of record, the distribution of responsibilities for the work shall be clearly identified for each IOR per CAC 7-141(f). One IOR shall be designated as the ‘lead' IOR per CAC 7-144(d). One IOR shall be assigned responsibility for “all other work” to make sure responsibility for the inspection of every part of the work is assigned.
INSPECTOR OF RECORD CAC 7-141, 7-145 & 7-151 |  | SCOPE OF INSPECTION | PERFORMED OFF-SITE
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## H-Plan Review
SECTION H |  | HCAI REVIEWED
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
NOTE: A structural engineer's signature is required for H and I projects or when they are substantially involved on an S project
Submitted By:
I have reviewed the approved construction documents for this project and all tests and special inspections required by Code are marked as “required” on this form.
Architect/Engineer of Record (Print Name) |  | Professional License # | Architect/Engineer of Record (Signature) | Date
Structural Engineer of Record (Print Name) |  | Professional License # | Structural Engineer of Record (Signature) | Date
FOR HCAI/OSHPD USE
TIO Program Reviewed by HCAI Plan Review Staff:
Note: HCAI plan review staff must provide verification that the TIO program has beeen "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## I-TIO Program Approval
SECTION I |  | TIO PROGRAM APPROVAL
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
This program is prepared and submitted for an OSHPD 2 or OSHPD 5 project. OSHPD 2 projects are limited to construction and remodel projects for: skilled nursing facilities and/or intermediate-care facilities of Type V, wood or light steel-frame construction (CBC 1225.1). OSHPD 5 projects are limited to construction and remodel projects for: acute psychiatric hospitals subject to licensure (CBC 1228.1).
Samples of Test and Special Inspection Reports are NOT required for laboratories approved through OPAA Program
All test and special inspection reports shall be submitted to the IOR, hospital owner, architect in responsible charge, and the structural engineer by the responsible approved agency and/or individual per CAC 7-149(a). The responisble approved agency and/or individual shall be employed by the health facility, owner, or governing board or authority per CAC 7-149(b).
Verified compliance reports shall be signed by the individual who performed the special inspection(s) as outlined in CAC 7-151(a). All reports shall clearly state whether the tests or special inspections were performed in accordance with the HCAI stamped approved documents and whether the results indicate compliance with those documents per CAC 7-149(a). All IORs performing special inspections shall hold the appropriate certification and equipment, and shall obtain approval from the design professional of record and HCAI prior to performing such work.
NOTE: This Test, Inspection, and Observation Report shall be approved by HCAI field personnel prior to start of construction.
Architect/Engineer of Record (Print Name) |  | Professional License # | Architect/Engineer of Record (Signature) | Date
FOR HCAI/OSHPD FIELD STAFF USE
TIO Program Approved by HCAI Field Staff:
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. HCAI Field staff will issue subsequent "TIO Program Approval". If "Approved with Comments" is checked the following comments shall be resolved by the designer prior to proceeding with the related construction:
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## J-Changes
SECTION J |  | CHANGES TO THE TIO PROGRAM
Facility #: | Facility Name: | Project #:
#NAME? | #NAME? | #NAME?
Notes: 1) A signature below indicates that the DPOR has verified the acceptance statements in Section I of this Form are applicable to any approved agencies/testing laboratories and special inspectors added. 2) All changes shall be approved as amended construction documents per CAC 7-153, or “concurred with” as non-material alterations per CAC 7-153(b), by HCAI prior to proceeding with the related work. 3) Structural Engineer of Record must only enter initials/date for changes that impact structural.
REVISION NUMBER | SYNOPSIS OF CHANGE | Architect/Engineer of Record (Initial/date) | Structural Engineer of Record (Initial/date) | DATE of Effective Change | HCAI/OSHPD Concurrence (Initial/Date)
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on D5: Enter a Revision Number for each change to the TIO Form
Note on E5: Brief description of the change to the form
Note on F5: Place initials in the box to indicate the architect or engineer in responsible charge has reviewed and approved the changes
Note on G5: Place initials in the box to indicate the structural engineer has reviewed and approved the changes (not required for changes which don't affect structural)
Note on H5: Effective date of the change

## Revision History
Revision number is shown at Section A, bottom right corner.
Version | Date | Description
R26.1 | 2026-01-16 | Revised version number to align with calendar year and month of release.
R26.1 | 2026-01-16 | Moved the Tab E Energy Code Compliance items to Tab C as special inspections. This is to align the spreadsheet version of the TIO with the upcoming eTIO.
R26.1 | 2026-01-16
R26.1 | 2026-01-16 | 2025 CBC: Added B-ME17, B-P22, B-P23, B-P24, B-E16, B-E17, B-E18, B-E19, B-E20, C-E8, C-E9, C-E10, C-E11
R26.1 | 2026-01-16 | 2022 CBC/2025 CBC: Added B-FP26
R26.1 | 2026-01-16 | 2022 CBC/2025 CBC: Removed B-E13, C-E5, C-E7
R26.1 | 2026-01-16 | 2022 CBC/2025 CBC: Moved C-A1 to C-FP8
R26.1 | 2026-01-16 | Added instructions on the "Macro Instructions" tab for when the "Compile error in hidden module" popup displays when opening the spreadsheet.
R26.1.1 | 2026-01-20 | 2022 CBC/2025 CBC: Moved C-A1 to C-FP8
R26.1.1 | 2026-01-20 | 2022 CBC/2025 CBC: Removed cell protections on user defined items
R26.1.2 | 2026-01-20 | 2022 CBC/2025 CBC: Fixed typos in tests and special inspections. Fixed '######' showing over Facility Number on Tab B.
R26.2 | 2026-02-06 | 2025 CBC: Updated code year on reference documents for Fire Protection And Life Safety System tests and special inspections.