## A-Project Info
Testing, Inspection, and Observation Program
2022 California Building Standards Code OSHPD 1
This program is prepared and submitted for an OSHPD 1 project. OSHPD 1 projects include all construction and remodel projects for: general acute care hospitals, acute psychiatric hospitals, and general acute care hospitals providing only acute medical rehabilitation center services (2022 CBC 1224.1).
SECTION A |  | PROJECT INFORMATION
Facility #: | Facility Name: |  | Project #:
Street Address:
City: |  | County:
Record Name (Scope of Project):
Abbreviations:
CAC: California Administrative Code |  | AAMA: American Architectural Manufacturers Association
CBC: California Building Code |  | NFPA: National Fire Protection Association
CEC: California Electrical Code |  | FM: FM Approval Standards
CMC: California Mechanical Code |  | DPOR: Design Professional of Record
CPC: California Plumbing Code
Testing, Inspection, and Observation Stages
Stage No. | Stage Name | Stage Scope / Description
1
DESIGN PROFESSIONAL OF RECORD RESPONSIBILITY
The administration of the work of construction, including this TIO, shall be under the responsible charge of an architect and structural engineer. When a structural engineer is not substantially involved, the architect shall be solely responsible. Where neither structural nor architectural elements are substantially involved, a mechanical or electrical engineer registered in the branch of engineering most applicable to the project may be in responsible charge. (CAC 7-141(a))
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
The "TIO Program Approval" from HCAI field staff must be obtained and included with the notice of start of construction required by CAC Section 7-137(a)4) and 7-145(a)5.A)
Construction shall not commence until the health facility has obtained from HCAI "TIO Program Approval". (CAC Section 7-135(a)3)
Note on I12: Project Number – As assigned by HCAI
Note on G15: Record Name (Scope of Project) – Scope of the project, as shown on the Application for New Project
Note on D23: TIO Stage Description - Provides a name and description/scope for each stage of a TIO program. Select the number of stages for your project by using the list box to the right of the project stage description. If the TIO program will be administered in a single stage then select "1 Stage". The number of stages on Tabs A, B, C, and D will automatically update when the number of stages is selected in the list box.

## B-Tests
|  |  | SECTION B |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | TESTS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Individual) | Compliance Verification by IOR (Initial/Date) | HCAI/FDD Use (Initial/Date)
x1 | STRUCTURAL TESTS
| x11 | Foundation
|  |  | B-F1 |  | Soil fill CBC 1705A.6 Fill material acceptance test
|  |  | B-F2 |  | Soil fill CBC 1705A.6 Compaction test
|  |  | B-F3 |  | Soil and rock anchors CBC 1811A Load test
|  |  | B-F4 |  | Deep foundation elements CBC 1810A.3.1.5.1, 1810A.3.3.1.2, 1810A.3.3.1.5, 1810A.3.3.2, & 1810A.3.10.4 Load test
|  |  | B-F5 |  | Shoring CBC 1812A Tie-Back Anchors
|  |  | B-F6 |  | Vibro Stone Columns (VSC) CBC 1813A Acceptance Test
B-F7
B-F8
| x12 | Concrete
|  |  | B-C1 |  | Concrete CBC 1705A.3, 1903A.6 & 1910A.1; ACI 318 1.9.1 & 26.4.1.1 Cementitious materials
|  |  | B-C2 |  | Concrete CBC 1705A.3, 1903A.5; ACI 318 1.9.1 & 26.4.1.2 Aggregates/Reactive aggregates
|  |  | B-C3 |  | Concrete CBC 1705A.3; ACI 318 26.4.1.4; ASTM C1602 Water
|  |  | B-C4 |  | Concrete CBC 1705A.3 & 1905A.1.17; ACI 318 26.12 Strength test
|  |  | B-C5 |  | Concrete CBC 1705A.3 & 1910A.2; ACI 318 20.2, 25.4.5.1 & 26.6.1.2 Metal reinforcement (including welded wire fabric and headed rebar)
|  |  | B-C6 |  | Concrete CBC 1705A.3, 1901A.3; ACI 318 20.4 Headed studs and headed stud assemblies
|  |  | B-C7 |  | Concrete CBC Table 1705A.3, 1903A.8 Weldability of reinforcing bars
|  |  | B-C8 |  | Concrete CBC 1705A.3 & 1910A.3; ACI 318 20.3, 25.8 & 26.6.1.2 Prestressing tendons and anchorage
|  |  | B-C9 |  | Concrete CBC 1911A.2; ACI 503.7 Crack repair by epoxy injection
|  |  | B-C10 |  | Concrete CBC 1911A.3; ICC-ES AC 178 § 9 Strengthening by externally bonded FRP
|  |  | B-C11 |  | Shotcrete CBC 1705A.3.9.2 & 1908A.2 Preconstruction test
|  |  | B-C12 |  | Shotcrete CBC 1705A.3.9 & 1908A.2 Strength test
|  |  | B-C13 |  | Post-installed anchors CBC 1910A.5 Installation verification test (includes adhesive, shot pins and mechanical anchors)
|  |  | B-C14 |  | Existing post-installed anchors CBC 1708A and CAC Ch 6, § 11.3 In-situ load tests
B-C15
B-C16
| x13 | Masonry
|  |  | B-MA1 |  | Masonry CBC 2105A.3 Mortar test
|  |  | B-MA2 |  | Masonry CBC 2105A.3 Grout test
|  |  | B-MA3 |  | Masonry CBC 2105A.2; TMS 602 1.4.B.3 Compressive strength f'm - prism test
|  |  | B-MA4 |  | Masonry CBC 2105A.4 Core test
|  |  | B-MA5 |  | Masonry CBC 1705A.4 Masonry anchors
|  |  | B-MA6 |  | Veneer CBC 1410.2 Veneer bond strength test
|  |  | B-MA7 |  | Architectural Cast Stone CBC 2103A.1 Strength of stone anchorage ASTM C1354
B-MA8
B-MA9
| x14 | Steel
|  |  | B-S1 |  | Steel CBC Table 1705A.2.1 & 2202A.1 Testing of unidentified steel or identification test for structural steel and cold formed steel
|  |  | B-S2 |  | Steel CBC 2213A.1 & 1705A.2.6 High strength bolts, nuts, and washers
|  |  | B-S3 |  | Steel CBC 2213A.2 & 1705A.2.5 End-welded studs
|  |  | B-S4 |  | Steel CBC 1705A.2.5 Nondestructive testing of welds
|  |  | B-S5 |  | Steel CBC 2205A.4 & 1705A.14.1 Nondestructive tests for seismic resistance
B-S6
B-S7
| x15 | Other Structural Materials
|  |  | B-OM1 |  | Aluminum CBC 2003.1 Testing
|  |  | B-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 AAMA 501.4 & 501.6 Tests - Exterior glass curtain walls
|  |  | B-OM3 |  | Thermal Barriers in Aluminum Mullion Systems CBC 2411.1.2 Testing of thermal barriers
B-OM4
B-OM5
| x16 | Alternative Systems
|  |  | B-AS1 |  | Seismic Isolation System CBC 1705A.14.4 Prototype and production test
|  |  | B-AS2 |  | Seismic Damping System CBC 1705A.14.4 Prototype and production test
|  |  | B-AS3 |  | Structural Design Criteria CBC 104.11.2 Tests to support alternative system
|  |  | B-AS4 |  | Wind Tunnel Testing CBC 1609A.1.1; ASCE 7 31.4 & 31.5; ASCE 49 Wind tunnel testing
B-AS5
B-AS6
| x17 | Nonstructural Components, Supports and Attachments
|  |  | B-N1 |  | Special Seismic Certification CBC 1705A.14.3 Shake table test
B-N2
B-N3
x2 | ELECTRICAL TESTS
|  |  | B-E1 |  | Ground Fault Protection of Equipment CEC 230.95(C) & 517.17(D)
|  |  | B-E2 |  | Emergency Systems/Generator Tests CEC 700.3(A) & NFPA 110-2019 § 7.13
|  |  | B-E3 |  | Automatic Transfer Switch Test NFPA 110-2019 § 7.13.4.1
|  |  | B-E4 |  | Emergency Stored Electrical Energy System Test NFPA 111-2019 § 7.6
|  |  | B-E5 |  | Grounding System in Patient Care Spaces 2018 NFPA 99 6.3.3.1
|  |  | B-E6 |  | Hospital Grade Receptacles 2018 NFPA 99 6.3.3.2.5
|  |  | B-E7 |  | Isolated Power Systems – Line Isolation Monitor Test 2018 NFPA 99 6.3.3.3.2
|  |  | B-E8 |  | Isolated Power Systems – Impedance of Isolated Wiring Test 2018 NFPA 99 6.3.2.9.2.1
|  |  | B-E9 |  | Medium Voltage Outdoor Systems Testing CEC 225.56
|  |  | B-E10 |  | Medium Voltage Cable Testing CEC 328.14, 225.56 & ANSI/NECA/NCSCB 600-2014
|  |  | B-E11 |  | Insulation Testing CEC 110.7
|  |  | B-E12 |  | Torque Electrical Connections CEC 110.3(B) & 110.14(D)
|  |  | B-E13 |  | Temporary Installation Grounding CEC 590.6
|  |  | B-E14 |  | Nurse Call System CEC 517.123
|  |  | B-E15 |  | Means of Egress Illumination CBC 1008.2 and 1008.3 Illumination and emergency power
B-E16
B-E17
x3 | MECHANICAL TESTS
|  |  | B-ME1 |  | Listed Hood Assemblies CMC 508.2
|  |  | B-ME2 |  | Type I Hood Capture and Containment Test CMC 511.2.2.2
|  |  | B-ME3 |  | Commercial Kitchen Hood Ventilation CMC 511.2.2.1 Performance test
|  |  | B-ME4 |  | Refrigeration Equipment CMC 1116.0
|  |  | B-ME5 |  | Refrigeration Detection and Alarm System CMC 1108.4 & CFC 608.7 Acceptance testing
|  |  | B-ME6 |  | Refrigeration Flaring System CMC 1114.3 Safety and effectiveness
|  |  | B-ME7 |  | Steam and Hot Water Boilers CMC 1013.0
|  |  | B-ME8 |  | Hydronics CMC 1205.2, 1220.4.6 & 1221.3 Pressure test of steam and water piping
|  |  | B-ME9 |  | Process Piping CMC 1405.2.2 Pressure test
|  |  | B-ME10 |  | Pre-Demolition Air Balance CMC 407.3.1 Pre-demolition air balance test and report
|  |  | B-ME11 |  | Post-Demolition Air Balance CMC 407.3.1 Air balance test and report
|  |  | B-ME12 |  | Ventilation System Air Balance CMC 407.3.1 & Table 4-A Areas tested and balanced
|  |  | B-ME13 |  | Duct Leakage Test CMC 603.9.2 SMACNA HVAC air duct leakage test
|  |  | B-ME14 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 416.4 Alarm system test
|  |  | B-ME15 |  | Airborne Infection Isolation Rooms and Protective Environment Rooms CMC 417.0 Mechanical system tested and balanced
B-ME16
B-ME17
x4 | PLUMBING TESTS
|  |  | B-P1 |  | Disinfection of Potable Water Systems CPC 609.10
|  |  | B-P2 |  | Medical Gas and Vacuum NFPA 99-2021 § 5.1.10.11.11 Qualification of brazing procedures and brazing
|  |  | B-P3 |  | Medical Gas and Vacuum NFPA 99-2021 § 5.1.12.2.1 thru 5.1.12.2.7 Installer performed tests |  |  | *ASSE 6010 Cert Req'd Input Responsible Individual
|  |  | B-P4 |  | Medical Gas and Vacuum NFPA 99-2021 § 5.1.12.2.6.7 & 5.1.12.2.7.6 Witness of 24-hour standing pressure test |  |  | *ASSE 6020 or 6030 Cert Req'd or Qualified IOR Input Responsible Individual
|  |  | B-P5 |  | Medical Gas and Vacuum NFPA 99-2021 § 5.1.12.3.1.1 thru 5.1.12.3.1.5 System inspection prior to concealment/cover |  |  | *ASSE 6020 or 6030 Cert Req'd Input Responsible Individual
|  |  | B-P6 |  | Medical Gas and Vacuum NFPA 99-2021 § 5.1.12.3.2.1 Inspection |  |  | *ASSE 6020 or 6030 Cert Req'd or Qualified IOR Input Responsible Individual
|  |  | B-P7 |  | Medical Gas and Vacuum NFPA 99-2021 § 5.1.12.4 System verification |  |  | *ASSE 6030 Cert Req'd Input Responsible Individual
|  |  | B-P8 |  | Existing Sewers and Drains CPC 102.4.1, 105.3, & 712.0 Tested for conformance with requirements for new work
|  |  | B-P9 |  | Water Supply System CPC 105.3 & 609.4 Pressure tested prior to covering or concealment
|  |  | B-P10 |  | Plumbing, Drainage, and Venting Systems CPC 105.3 & 712.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P11 |  | Building Sewer CPC 105.3, 712.0, & 723.0 Water or air tested prior to use, covering or concealment. No air test for plastic piping.
|  |  | B-P12 |  | Storm Drain Piping CPC 1107.0 Water or air tested prior to use, covering or concealment
|  |  | B-P13 |  | Fuel Gas Piping CPC 1213.0 & CMC 1313.0 Air, CO2 or nitrogen tested prior to use, covering, or concealment
|  |  | B-P14 |  | Private Sewer Disposal System CPC 105.0, & CPC Appendix H H1001.2 Tested prior to use, covering, or concealment
|  |  | B-P15 |  | Protectively Coated Pipe CPC 312.5 Tested for voids, damage, and imperfections
|  |  | B-P16 |  | Defective Systems CPC 105.3.1, 105.3.2, 712.0 Air test of defective drainage and plumbing systems
|  |  | B-P17 |  | Shower Receptors CPC 408.7.5
|  |  | B-P18 |  | Backflow Prevention Devices and Assemblies CPC 603.2 & 603.4.2 Assembly tested
|  |  | B-P19 |  | Non-Potable Water CPC 1502.0 Testing of alternate water sources and cross-connections
|  |  | B-P20 |  | Recycled Water Supply Systems CPC 1505.5 & 1505.13 Initial cross-connection test and system testing before initial operation
|  |  | B-P21 |  | On-Site Treated Non-Potable Gray Water Systems CPC 1502.1, 1506.5, & 1506.12 Initial cross-connection test and system testing before initial operation
B-P22
B-P23
B-P24
x5 | FIRE PROTECTION AND LIFE SAFETY SYSTEMS
|  |  | B-FP1 |  | Fire Alarm CFC 901.5 & CFC 907.7 NFPA 72-2022 §14.4 Acceptance and reacceptance testing
|  |  | B-FP2 |  | Fire and Smoke Dampers CFC 901.5 & CFC 907.8 Acceptance testing
|  |  | B-FP3 |  | Duct Detectors CFC 901.5, NFPA 72-2022 §14.4 Differential pressure test
|  |  | B-FP4 |  | Smoke Control System CFC 901.5, CFC 909.18 & 1705A.19 Acceptance testing
|  |  | B-FP5 |  | Fire Sprinkler CFC 901.5 & NFPA 13-2022 Chapter 29 Above ground piping acceptance testing
|  |  | B-FP6 |  | Fire Sprinkler CFC 901.5 & NFPA 13-2022 Chapter 29 Underground piping acceptance testing
|  |  | B-FP7 |  | Standpipe System CFC 901.5 & NFPA 14-2019 Chapter 11 Above ground piping acceptance testing
|  |  | B-FP8 |  | Standpipe System CFC 901.5, CFC 905.3.1 & NFPA 14-2019 Chapter 11 Acceptance testing in buildings 4-stories or more
|  |  | B-FP9 |  | Standpipe System CFC 901.5 & NFPA 14-2019 Chapter 11 Underground piping acceptance testing
|  |  | B-FP10 |  | Private Fire Mains CFC 901.5 & NFPA 24-2019 § 10.10 Acceptance testing
|  |  | B-FP11 |  | Fire Pumps CFC 901.5 & NFPA 20-2019 § 14.1 & 14.2 Acceptance testing
|  |  | B-FP12 |  | Fire Protection Water Tank CFC 901.5 & NFPA 22-2018 Chapter 17 Acceptance testing
|  |  | B-FP13 |  | Wet Chemical Extinguishing System CFC 901.5 & NFPA 17A-2021 § 7.4 Acceptance testing
|  |  | B-FP14 |  | Clean Agent Extinguishing System CFC 901.5 & NFPA 2001-2018 § 7.7 Acceptance testing
|  |  | B-FP15 |  | CO2 Extinguishing System CFC 901.5 & NFPA 12-2018 § 4.4.3 & 4.4.4 Acceptance testing
|  |  | B-FP16 |  | Dry Chemical Extinguishing System CFC 901.5 & NFPA 17-2021 § 10.4 Acceptance testing
|  |  | B-FP17 |  | Halon 1301 Extinguishing System CFC 901.5 & NFPA 12A-2018 § 6.7 Acceptance testing
|  |  | B-FP18 |  | Underground Fuel Storage Tank CFC 5704.2.12 & NFPA 30-2021 § 21.5.1 Initial testing
|  |  | B-FP19 |  | Underground Fuel Storage Tank CFC 5704.2.12 & NFPA 30-2021 § 21.5.2 Tightness testing
|  |  | B-FP20 |  | Flammable and Combustible Liquid Fuel Piping CFC 5703.6.3 Pressure testing
|  |  | B-FP21 |  | Emergency Responder Radio Coverage CFC 510.5.4 Acceptance test procedure
|  |  | B-FP22 |  | Testing of Elevator Shutdown CBC 3005.5, NFPA 72-2022 21.4, & ASME A17.1/CSA B44-2019
|  |  | B-FP23 |  | Elevator Emergency Operation CBC 3003.2 Emergency recall and in-cart operation
|  |  | B-FP24 |  | Elevator Emergency Standby Power CBC 3003.1 Backup generator engaged
|  |  | B-FP25 |  | Fire Door, Fire Shutter, and Fire Windows NFPA 80-2019 5.2 Testing
B-FP26
B-FP27
x6 | OTHER TESTS
|  |  | B-OT1 |  | Radiation Shielding Barriers CBC 1705A.1.1 and 3102C Radiation shielding barrier test
|  |  | B-OT2 |  | Manufacturer Required Tests
|  |  | B-OT3 |  | Designer Required Tests
B-OT4
B-OT5
B-OT6
B-OT7
B-OT8
B-OT9
B-OT10
Note on D3: Project information in this row is referenced from Tab A-Project Info
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on F5: Blank rows are provided to add any additional tests which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F52: Required for projects that use aluminum as a structural material.
Note on F53: Required for projects that include glazing scope that uses structrual sealant.
Note on F54: This is for HCAI 1, 1R, 2, 4 & 5. The requirements of this section address the testing and inspection of thermal barriers composite in aluminum mullion systems.
Note on F58: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F59: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F60: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F65: Required on projects where equipment requiring special seismic certification has not been preapproved or justified by analysis.
Note on F69: For 480V electrical "service" rated 1000A or more, and a feeder meeting CEC 215.10. (NOT FOR GFCI TESTING).
Note on F70: For new and replacement emergency generator installations.
Note on F71: For new and replacement automatic transfer switch installations.
Note on F72: Testing of UPS and other battery storage systems used as energy storage system. Note: An UPS supplied by an emergency power supply system (EPSS) like an essential electrical system is not required to be tested to NFPA 111.
Note on F73: Voltage and impedance measurements when new electrical circuits and receptacles are installed in patient care spaces like head walls.
Note on F74: Recepacle retention force test when new receptacles are installed in patient care spaces like head walls
Note on F75: For Operating Room / Wet Procedures with isolated power systems
Note on F76: For Operating Room / Wet Procedures. Related to Isolated Power System - Line Isolation monotor test
Note on F77: Medium voltage (over 1000v) may be used for a large hospital campus. Pre-energization and operational tests for new and modified electrical systems over 1000V.
Note on F78: Testing of new medium volt cables (1kv - 100kv). Related to Medium Voltage Outdoor Systems – Inspections and Test.
Note on F79: Megger test of new conductors to ensure wiring is free from short circuits and ground faults.
Note on F80: For panelboards, switchboards, switchgear, MCC, and other electrical equipment that require electrical connections to be torqued per manufacture instructions.
Note on F81: For temporary work.
Note on F82: For new or modified nurse call systems. This is a functional test.
Note on F87: Listed hood assemblies shall be tested in accordance with UL 710 or equivalent. Listed UV hood assemblies shall be tested in accordance with UL 710 or UL 710C.
Note on F88: Listed hood assemblies shall be tested per manufacturer. Listed UV hoods tested IAW UL 710 and 710C.
Note on F89: Performance test before final approval of install of ventilation system.
Note on F90: Factory and field refrigeration system pressure testing.
Note on F91: Alarm system testing of machinery room alarm systems.
Note on F92: Report for approved agency detailing emission products.
Note on F93: Inspection and test protocol for boilers after installation and prior to use.
Note on F94: Pressure testing for system piping and components. Note: piping to be installed in concrete shall be tested per these requirements prior to pouring concrete.
Note on F95: Pressure test at completion of installation.
Note on F96: Survey of exisitng ventilation system priory to start of remodel work.
Note on F97: Survey of ventilation system at completion of remodel work to ensure pre-demolition air balance values are maintained.
Note on F98: Test and balance of new spaces, spaces affected by new equipment or spaces with change in function after completion of work.
Note on F100: Testing of air pressure alarm systems prior to acceptance.
Note on F101: Test and balance of mechanical system after completion of work.
Note on F105: Testing to be done for new piping and when pipes have been breached in project. Not for fixture replacement.
Note on F106: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F107: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F108: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F109: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F110: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F111: Testing shall be performed on all new piped medical gas and vacuum systems, additions, renovations, temporary installations, or repaired systems.
Note on F112: Testing for modified or breached sewer piping.
Note on F113: Testing of completion of new segment or entire system.
Note on F116: Water or air testing for new storm drain piping, and parts of existing storm drain piping that have been altered, extended, or repaired.
Note on F117: Testing required for new, or repaired fuel piping prior to acceptance and initial operation.
Note on F118: Static and fluid water testing after installation.
Note on F120: Air testing of existing drainage or plumbing that is suspected to be defective.
Note on F121: Standing water test for drain/receptor interface.
Note on F122: Device shall be approved by the AHJ and then tested at time of installation, repair, or relocation.
Note on F123: Testing of all new alternate water sources for nonpotable water including testing emphasis on cross-connection prevention.
Note on F130: For new installations, remodels, replacements or repairs. When required, test when interconnected with other systems. and before the occupancy of the building or specific area.
Note on F131: Shall be tested when the system is altered or modified. When required, test when interconnected with other systems.
Note on F132: For new installations, remodels, replacements, repairs, or when there are changes to the site-specific software. When required, test when interconected with other systems. Shall notify HCAI and owner prior to initial acceptance test.
Note on F133: For new installations, remodels, replacements or repairs. When required, test when interconnected with other systems. Test shall include function, sequence and, where applicable, capacity of their installed condition. Test shall be prior to concelement and prior to occupancy.
Note on F134: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F135: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F136: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independetly. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F137: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independetly. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F138: For new installations, remodels, replacements or repairs. In existing system new pipe shall be tested independetly. During construction, existing standpipes shall be maintained in working order and always ready for use.
Note on F139: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test.
Note on F140: For new installations, remodels, replacements or repairs. If components that affect performance are replaced, then a retest shall be conducted by the pump manufacturer or designated representative or qualified persons acceptable to HCAI.
Note on F141: For new installations, remodels, replacements or repairs. Shall notify HCAI and owner prior to initial acceptance test. Prior to placing the tank in service, a representative of the tank contractor and a representative of the owner shall conduct a joint inspection of the completed equipment.
Note on F142: For new installations, remodels, replacements or repairs.
Note on F143: For new installations, remodels, replacements or repairs.
Note on F144: For new installations, remodels, replacements or repairs.
Note on F145: For new installations, remodels, replacements or repairs.
Note on F146: For new installations, remodels, replacements or repairs.
Note on F147: For new installations, remodels, replacements or repairs.
Note on F148: For new installations, remodels, replacements or repairs.
Note on F149: For new installations, remodels, replacements or repairs.
Note on F150: For new installations, remodels, replacements or repairs.
Note on F151: For new installations, remodels, replacements or repairs.
Note on F152: For new installations, remodels, replacements or repairs.
Note on F153: For new installations, remodels, replacements or repairs.
Note on F154: For new installations, remodels, replacements or repairs.
Note on F158: Required on all projects that contain imaging equipment radiation shielding barriers.

## C-On-Site Special Inspections
|  |  | SECTION C |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | ON-SITE SPECIAL INSPECTIONS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Special Inspector) | Compliance Verification by IOR (Initial/Date) | HCAI/FDD Use (Initial/Date)
x1 | STRUCTURAL SPECIAL INSPECTIONS
| x11 | Foundation
|  |  | C-F1 |  | Soils CBC 1705A.6 Soil fill
|  |  | C-F2 |  | Foundation CBC 1705A.7 Driven deep foundations
|  |  | C-F3 |  | Foundation CBC 1705A.8 Cast-in-place deep foundations
|  |  | C-F4 |  | Foundation CBC 1705A.9 Helical pile foundations
|  |  | C-F5 |  | Shoring CBC 1812A Shoring
|  |  | C-F6 |  | Vibro Stone Columns (VSC) CBC 1813A Vibro stone columns
|  |  | C-F7 |  | Prestressed Soil and Rock Anchors CBC 1811A & 1812A Installation and testing
C-F8
C-F9
| x12 | Concrete
|  |  | C-C1 |  | Concrete CBC 1705A.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | C-C2 |  | Concrete CBC 1705A.3; ACI-318 26.4.1.5 Admixtures
|  |  | C-C3 |  | Concrete CBC 1705A.3; ACI-318 26.4 Mix design
|  |  | C-C4 |  | Concrete CBC 1705A.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | C-C5 |  | Concrete CBC 1705A.3 CIP & post-installed anchors
|  |  | C-C6 |  | Concrete CBC Table 1705A.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | C-C7 |  | Concrete CBC 1705A.3; ACI-318 26.13 Specialty inserts, stud rails, rebar mechanical connections, headed rebar
|  |  | C-C8 |  | Concrete CBC 1705A.3.4; ACI-318 26.13 Prestressed concrete
|  |  | C-C9 |  | Concrete CBC 1705A.3; ACI 318 26.9, 26.13.1 & 26.13.3.3 Precast concrete erection
|  |  | C-C10 |  | Shotcrete CBC 1705A.3.9 & 1908A Installation
|  |  | C-C11 |  | Concrete CBC 1705A.3 Insulating concrete
|  |  | C-C12 |  | Concrete CBC 1705A.3, 1705A.3.1 & 1903A.8 Welding of reinforcing bars
|  |  | C-C13 |  | Concrete PCI MNL 128 standard GFRC panels
|  |  | C-C14 |  | Concrete CBC 1911A.2; ACI 503.7 Crack repair by epoxy injection
|  |  | C-C15 |  | Concrete CBC 1911A.3, ICC AC178 § 3 to 8 Strengthening by externally bonded FRP
C-C16
C-C17
| x13 | Masonry
|  |  | C-MA1 |  | Masonry CBC 1705A.4 Laying and grouting
|  |  | C-MA2 |  | Masonry CBC 2104A.1.3 Reinforced grouted masonry
|  |  | C-MA3 |  | Masonry CBC 1705A.4 Masonry anchors
C-MA4
C-MA5
| x14 | Steel
|  |  | C-S1 |  | Steel CBC 1705A.2.1 & 1705A.2.5 Automatic end-welded studs
|  |  | C-S2 |  | Steel CBC 1705A.2.5 Field welding
|  |  | C-S3 |  | Steel AWS D1.1 3 & 4 & AWS D1.8 6.1 Field welding - WPS / WPQR
|  |  | C-S4 |  | Steel CBC 1705A.2 & 1705A.2.6 High strength bolt installation
|  |  | C-S5 |  | Steel CBC 1705A.2, 1705A.12.2, & 1705A.13.3 Cold-formed steel light frame construction
|  |  | C-S6 |  | Steel CBC 1705A.13 Special inspections for seismic resistance
C-S7
C-S8
| x15 | Wood
|  |  | C-W1 |  | Wood CBC 1705A.5, 1705A.5.5, & 1705A.12.1 Glue laminated timber
|  |  | C-W2 |  | Wood CBC 1705A.5.6, 1705A.11.1, & 1705A.12.1 Installation of timber connectors
|  |  | C-W3 |  | Wood CBC 1705A.5, 1705A.5.2, & 1705A.5.6 Manufactured trusses
|  |  | C-W4 |  | Wood CBC 1705A.12.1 & 1705A.13.2 Nailing, screw attachment, bolting, anchoring, field gluing operations, and other fastening
C-W5
C-W6
| x16 | Other Structural Materials
|  |  | C-OM1 |  | Aluminum CBC 2003.1 Inspection
|  |  | C-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 & 1705A.13.5.2 Structural sealants for exterior glass curtain walls
|  |  | C-OM3 |  | Thermal Barriers in Aluminium Mullion Systems CBC 2411.1.2 Testing and inspection
C-OM4
C-OM5
| x17 | Alternative Systems
|  |  | C-AS1 |  | Alternative system CBC 1705A.1.1 Construction materials and methods for alternative system
|  |  | C-AS2 |  | Seismic Isolation System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
|  |  | C-AS3 |  | Seismic Damping System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
C-AS4
C-AS5
| x18 | Nonstructural components, supports and attachments
|  |  | C-N1 |  | Architectural components CBC 1705A.13.5 & 1705A.17 Cladding, nonbearing walls, and veneer
|  |  | C-N2 |  | Ceiling CBC 1705A.13.5 Suspended ceiling systems and their anchorage
|  |  | C-N3 |  | Access floors CBC 1705A.13.5.1 Anchorage of access floor systems
|  |  | C-N4 |  | Storage racks 8’ or taller CBC 1705A.13.7 Anchorage
|  |  | C-N5 |  | Plumbing, mechanical and electrical components CBC 1705A.13.6 Anchorage, bracing, and vibration isolators
|  |  | C-N6 |  | Special Seismic Certification CBC 1705A.13.4 Special seismic certification label, anchorage, and mounting
C-N7
C-N8
x2 | ELECTRICAL INSPECTIONS
|  |  | C-E1 |  | Available Fault and Short-Circuit Current Field Marking per Approved Coordination Study CEC 110.16(B), 110.24(A), 620.51(D)(1), & 700.5(E)
|  |  | C-E2 |  | Essential Electrical System Adjustable Circuit Breaker Selection and Settings per Approved Coordination Study CEC 517.31(G)
|  |  | C-E3 |  | Elevator Selective Adjustable Circuit Breaker Selection and Settings per Approved Coordination Study CEC 620.62
|  |  | C-E4 |  | Fire Pump Circuit Breaker Selection and Settings per Approved Coordination Study CEC 695.3(C)(3)
|  |  | C-E5 |  | Arc Energy Reduction CEC 240.67 & 240.87
|  |  | C-E6 |  | Short-Circuit Current Calculations CEC 110.24(A), 409.22, 430.99, 440.10(B)
|  |  | C-E7 |  | Arc Flash Hazard Warning CEC 110.16(A)
C-E8
C-E9
x3 | MECHANICAL INSPECTIONS
C-M1
C-M2
x4 | PLUMBING INSPECTIONS
C-P1
C-P2
x5 | FIRE PROTECTION AND LIFE SAFETY SYSTEM SPECIAL INSPECTIONS
|  |  | C-FP1 |  | Sprayed Fire-Resistant Materials CBC 1705A.15 Spray-applied fireproofing
|  |  | C-FP2 |  | Mastic and Intumescent Fire-Resistant Coatings CBC 1705A.16 In accordance with AWCI 12-B
|  |  | C-FP3 |  | Penetration Firestops CBC 1705A.18.1 Penetration firestop systems that are tested and listed
|  |  | C-FP4 |  | Fire-Resistant Joint Systems CBC 1705A.18.2 Fire-resistant joint systems that are tested and listed
|  |  | C-FP5 |  | Smoke Control Systems CFC 909.18.8, CBC 170.17, & 1705A.19 Ductwork and operation
|  |  | C-FP6 |  | Sprinkler System Piping NFPA 13-2022 § 7.5.2 Welded pipe and fittings
|  |  | C-FP7 |  | Standpipe System Piping NFPA 14-2019 § 4.4.2 Welded pipe and fittings
|  |  | C-FP8 |  | Fire Door, Fire Shutter, and Fire Windows NFPA 80-2019 5.1.4, 5.2 Inspection and labeling
C-FP9
C-FP10
x6 | OTHER SPECIAL INSPECTIONS
|  |  | C-OT1 |  | Exterior insulation and finish systems (EIFS). CBC 1705A.17 EIFS applications
|  |  | C-OT2 |  | Water-resistive barrier coating CBC 1705A.17.1 ASTM E2570 barrier coating when installed over a sheathing substrate
|  |  | C-OT3 |  | Exit Signs CBC 1013.1 Location, illumination and physical characteristics
|  |  | C-OT4 |  | Accessible Signage CBC 11B-703.1 Visual and tactile requirements
C-OT5
C-OT6
C-OT7
C-OT8
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F58: Required for projects that use aluminum as a structural material.
Note on F59: Required for projects that include glazing scope that uses structrual sealant.
Note on F64: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F65: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F66: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F74: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F75: Required on projects with equipment requiring special seismic certification.
Note on F80: Study required from the Electrical Engineer of Record (EEOR) when new circuit breakers and fuses are installed in new and existing essential electrical systems. Single line diagram and over current protective devices in study shall match approved electrical plans. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F81: Applies to elevator, elevators, dumbwaiters, escalators, moving walks, platform lifts, and stairway chairlifts installations. Study required from the Electrical Engineer of Record (EEOR) when more than one machine is fed from one feeder. Single line diagram and over current protective devices in study shall match approved electrical plans. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F82: Not required for most fire pump installations. Only for new fire pumps in multi-building campus style complexes. Study to be used to set and verify all adjustable circuit breakers settings.
Note on F83: For 1200amp or larger electrical equipment installations.
Note on F84: Required for new panelboards, switchboards, switchgear, MCC, ATS, and elevator controllers. Study from the Electrical Engineer of Record (EEOR) for stating all new electrical equipment SCCR/AIC ratings meet or exceed available fault currents values determined in the study. Study used in the field to verify installed equipment SCCR/AIC match the information provided in the study.
Note on F85: Electrical equipment that is likely to require examination, adjustment, servicing, or maintenance while energized, shall be field or factory marked to warn qualified persons of potential electric arc flash hazards.
Note on F95: For new, remodel, or replacement projects. This type of test is applied to floor, roof, and wall assemblies, and structural members. Consider OPD-0091-13 for Fire-Resistive Standard Details.
Note on F96: Applicable for structural elements on new, remodel, or replacement projects.
Note on F97: For new, remodel, or replacement projects.
Note on F98: For new, remodel, or replacement projects.
Note on F99: For new, remodel, or replacement projects when having erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location. Also prior to occupancy and after sufficient completion for the purposes of pressure-difference testing, flow measurements, and detection and control verification.
Note on F100: For new, remodel, or replacement projects when there is welding sprinkler pipe.
Note on F101: For new, remodel, or replacement projects when standpipe system piping is welded.
Note on F102: For new installations, remodels, replacements or repairs.

## D-Off-Site Special Inspections
|  |  | SECTION D |  |  | NOTE: Approved agencies, individuals, and all changes to the TIO program shall be identified, evaluated by the DPOR and approved by HCAI prior to proceeding with the related work.
|  |  | Facility #: |  | Facility Name: | Project #:
Select with "X" or provide required OPAA information:
|  |  | Index # | Stage 1 Required (Select with "X") | OFF-SITE SPECIAL INSPECTIONS | Samples of Test & Inspection Reports Included | OPAA No. and Expiration Date | Responsible Approved Agency And/Or Individual (Identify Special Inspector) | Compliance Verification by IOR (Initial/Date) | HCAI/FDD Use (Initial/Date)
x1 | STRUCTURAL SPECIAL INSPECTIONS
| x11 | Concrete
|  |  | D-C1 |  | Concrete CBC 1705A.3; ACI-318 26.5.2 & 26.13 Placement of concrete
|  |  | D-C2 |  | Concrete CBC 1705A.3; ACI-318 26.4.1.5 Admixtures
|  |  | D-C3 |  | Concrete CBC 1705A.3; ACI-318 26.4 Mix design
|  |  | D-C4 |  | Concrete CBC 1705A.3; ACI-318 26.13 Reinforcing steel & prestressing steel
|  |  | D-C5 |  | Concrete CBC 1705A.3 CIP & post-installed anchors
|  |  | D-C6 |  | Concrete CBC Table 1705A.3 Adhesive anchors in horizontal and upwardly inclined positions with sustained tension load
|  |  | D-C7 |  | Concrete CBC 1705A.3; ACI-318 26.13 Specialty inserts, stud rails, rebar mechanical connections, headed rebar
|  |  | D-C8 |  | Concrete CBC 1705A.3.3 Batch plant inspection
|  |  | D-C9 |  | Concrete CBC 1705A.3.4; ACI-318 26.13 Prestressed concrete
|  |  | D-C10 |  | Concrete CBC 1705A.3 Insulating concrete
|  |  | D-C11 |  | Concrete CBC 1705A.3, 1705A.3.1 & 1903A.8 Welding of reinforcing bars
|  |  | D-C12 |  | Concrete PCI MNL 128 standard GFRC panels
D-C13
D-C14
| x12 | Masonry
|  |  | D-MA1 |  | Masonry CBC 1705A.4 Masonry anchors
D-MA2
D-MA3
| x13 | Steel
|  |  | D-S1 |  | Steel CBC 1705A.2; AISC 360 & AISC 341 Steel shop fabrication
|  |  | D-S2 |  | Steel CBC 1705A.2.1 & 1705A.2.5 Automatic end-welded studs
|  |  | D-S3 |  | Steel CBC 1705A.2.5 Shop welding
|  |  | D-S4 |  | Steel AWS D1.1 3 & 4 and AWS D1.8 6.1 Shop welding - WPS / WPQR
|  |  | D-S5 |  | Steel CBC 1705A.2 & 1705A.2.6 High strength bolt installation
|  |  | D-S6 |  | Steel CBC 1705A.2, 1705A.12.2, & 1705A.13.3 Cold-formed steel light frame construction
|  |  | D-S7 |  | Steel CBC 1705A.13 Special inspections for seismic resistance
D-S8
D-S9
| x14 | Wood
|  |  | D-W1 |  | Wood CBC 1705A.5, 1705A.5.5, & 1705A.12.1 Glue laminated timber
|  |  | D-W2 |  | Wood CBC 1705A.5.6, 1705A.11.1, & 1705A.12.1 Installation of timber connectors
|  |  | D-W3 |  | Wood CBC 1705A.5, 1705A.5.2, & 1705A.5.6 Manufactured trusses
|  |  | D-W4 |  | Wood CBC 1705A.12.1 & 1705A.13.2 Nailing, screw attachment, bolting, anchoring, field gluing operations, and other fastening
D-W5
D-W6
| x15 | Other Structural Materials
|  |  | D-OM1 |  | Aluminum CBC 2003.1 Inspection
|  |  | D-OM2 |  | Structural Sealant Glazing CBC 2410.1.2 & 1705A.13.5.2 Structural sealants for exterior glass curtain walls
|  |  | D-OM3 |  | Thermal Barriers in Aluminium Mullion Systems CBC 2411.1.2 Testing and inspection
D-OM4
D-OM5
| x16 | Alternative Systems
|  |  | D-AS1 |  | Alternative system CBC 1705A.1.1 Construction materials and methods for alternative system
|  |  | D-AS2 |  | Seismic Isolation System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
|  |  | D-AS3 |  | Seismic Damping System CBC 1705A.13.8 Fabrication, installation, prototype, and production testing
D-AS4
D-AS5
| x17 | Nonstructural components, supports and attachments
|  |  | D-N1 |  | Architectural Components CBC 1705A.13.5 & 1705A.17 Cladding, nonbearing walls, and veneer
|  |  | D-N2 |  | Ceiling CBC 1705A.13.5 Suspended ceiling systems and their anchorage
|  |  | D-N3 |  | Access Floors CBC 1705A.13.5.1 Anchorage of access floor systems
|  |  | D-N4 |  | Storage Racks 8’ or Taller CBC 1705A.13.7 Anchorage
|  |  | D-N5 |  | Plumbing, Mechanical, and Electrical Components CBC 1705A.13.6 Anchorage, bracing, and vibration isolators
|  |  | D-N6 |  | Special Seismic Certification CBC 1705A.13.4 Special seismic certification label, anchorage, and mounting
D-N7
D-N8
x2 | MECHANICAL INSPECTIONS
D-M1
D-M2
x3 | PLUMBING INSPECTIONS
D-P1
D-P2
x4 | FIRE PROTECTION AND LIFE SAFETY SYSTEMS SPECIAL INSPECTIONS
|  |  | D-FP1 |  | Sprayed Fire-Resistant Materials CBC 1705A.15 Spray-applied fireproofing
|  |  | D-FP2 |  | Mastic and Intumescent Fire-Resistant Coatings CBC 1705A.16 In accordance with AWCI 12-B
|  |  | D-FP3 |  | Penetration Firestops CBC 1705A.18.1 Penetration firestop systems that are tested and listed
|  |  | D-FP4 |  | Fire-Resistant Joint Systems CBC 1705A.18.2 Fire-resistant joint systems that are tested and listed
|  |  | D-FP5 |  | Smoke Control Systems CFC 909.18.8 & CBC 170.17 & 1705A.19 Ductwork and operation
|  |  | D-FP6 |  | Sprinkler System Piping NFPA 13-2022 § 7.5.2 Welded pipe and fittings
|  |  | D-FP7 |  | Standpipe System Piping NFPA 14-2019 § 4.4.2 Welded pipe and fittings
D-FP8
D-FP9
x5 | OTHER SPECIAL INSPECTIONS
|  |  | D-OT1 |  | Exterior Insulation and Finish Systems (EIFS) CBC 1705A.17 EIFS applications
|  |  | D-OT2 |  | Water-Resistive Barrier Coating CBC 1705A.17.1 ASTM E2570 barrier coating when installed over a sheathing substrate
D-OT3
D-OT4
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional special inspections which may be required
Note on I5: Name of the OSHPD approved agency (or in some cases the individual) approved to perform the test (See Section/Tab I)
Note on J5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted
Note on F44: Required for projects that use aluminum as a structural material.
Note on F45: Required for projects that include glazing scope that uses structrual sealant.
Note on F50: Required for projects that include work that is unusual in nature. Work that includes construction with alternatives to traditional materials and/or systems, unusual design applications, and/or manufacturer installation requirements that are not shown in codes or standards.
Note on F51: Required for projects that include seismic isolators as part of the lateral force resisting system.
Note on F52: Required for projects that include energy dissipation devices as part of the lateral force resisting system.
Note on F60: This is generally required on most new and remodel projects that include the installation or revisions to existing distributive utility systems and their associated equipment.
Note on F61: Required on projects with equipment requiring special seismic certification.
Note on F71: For new, remodel, or replacement projects. This type of test is applied to floor, roof, and wall assemblies, and structural members. Consider OPD-0091-13 for Fire-Resistive Standard Details.
Note on F72: Applicable for structural elements on new, remodel, or replacement projects.
Note on F73: For new, remodel, or replacement projects.
Note on F74: For new, remodel, or replacement projects.
Note on F75: Applicable for new, remodel, replacement, repair projects when having erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location. Also prior to occupancy and after sufficient completion for the purposes of pressure-difference testing, flow measurements, and detection and control verification.
Note on F76: For new, remodel, or replacement projects when there is welding sprinkler pipe.
Note on F77: For new, remodel, or replacement projects when standpipe system piping is welded.

## E-Required Compliance Forms
|  |  | SECTION E |  |  | REQUIRED COMPLIANCE FORMS
|  |  | Facility #: |  | Facility Name: | Project #:
|  |  | Form # | Required (Select with "X") | DOCUMENT NAME | Responsible Designer Or Installing Contractor | Compliance Verification by IOR (Initial/Date) | HCAI/FDD Use (Initial/Date)
x1 | CALIFORNIA ENERGY CODE
| x11 | NON-RESIDENTIAL CERTIFICATE OF INSTALLATION (NRCI)
|  |  | NRCI-ENV-01-E |  | ENVELOPE
|  |  | NRCI-MCH-01-E |  | MECHANICAL
|  |  | NRCI-PLB-01-E |  | PLUMBING
|  |  | NRCI-LTI-01-E |  | INDOOR LIGHTING (conditioned, processed spaces)
|  |  | NRCI-LTI-02-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTI-04-E |  | TWO INTERLOCKED LIGHTING SYSTEMS (conditioned, processed spaces)
|  |  | NRCI-LTI-05-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTI-06-E |  | VIDEO CONFERENCE STUDIO LIGHTING (conditioned, processed spaces)
|  |  | NRCI-LTI-01-E |  | INDOOR LIGHTING (conditioned, processed spaces)
|  |  | NRCI-LTI-02-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTI-05-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (conditioned, processed spaces)
|  |  | NRCI-LTO-01-E |  | OUTDOOR LIGHTING
|  |  | NRCI-LTO-02-E |  | ENERGY MANAGEMENT CONTROL SYSTEM OR LIGHTING CONTROL SYSTEM (outdoor lighting)
|  |  | NRCI-ELC-01-E |  | ELECTRICAL POWER DISTRIBUTION
|  |  | NRCI-PRC-01-E |  | COVERED PROCESSES (commercial refrigeration)
|  |  | NRCI-PRC-01-E |  | COVERED PROCESSES (parking garage)
|  |  | NRCI-PRC-01-E |  | COVERED PROCESSES (process boilers greater than 2.5 MM Btu/h)
|  |  | NRCI-LTS-01-E |  | SIGN LIGHTING (indoor and outdoor)
| x12 | NON-RESIDENTIAL CERTIFICATE OF ACCEPTANCE (NRCA)
|  |  | NRCA-ENV-02-F |  | FENESTRATION ACCEPTANCE
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on A5: Click on the '+' sign to expand the section of the form. Click on the '-' sign to collapse the section
Note on D5: Note: Reference numbers will not be sequential once the form is compiled
Note on E5: Place an 'X' in this column to indicate the test is required
Note on F5: Blank rows are provided to add any additional documentation required by local AHJs or other entities specific to the project
Note on G5: Name of the installing contractor which under their purview the items were installed and/or to meet the requirements documented in the NRCC, NRCA and approved construction documents
Note on I5: The IOR shall place their initials and date in this column to indicate all of the required testing for the item is satisfactorily completed and accepted

## F-Cons Verif
SECTION F |  |  | CONSTRUCTION VERIFICATION
Facility #: | Facility Name: | [7 empty] | Project #:
VERIFIED CONSTRUCTION INSPECTION AND OBSERVATION REPORTING | [11 empty] | HCAI/FDD USE
REFERENCE NUMBER |  | PROJECT STAGE(S), MILESTONE, OR INTERVAL (Clearly indicate which Stage(s) apply to which Milestone/Interval) | VERIFIED COMPLIANCE REPORT REQUIRED AS INDICATED (Form HCAI-OSH-123) (See “PERSONAL KNOWLEDGE” as defined in California Administrative Code, Section 7-151)
|  |  | GEOR | AOR | SEOR | MEOR | EEOR | CONT | IOR | SP INSP | TEST LAB
Clear all plan review Outstanding Items List (OIL) Items
Installation of Temporary Equipment
Removal of Temporary Equipment
Substantial Compliance (Remodel, Renovations, Maintenance projects, Equipment Replacement)
Certificate of Occupancy (New Buildings, Additions, Changes in Occupancy)
Construction Final
ABBREVIATIONS: |  | GEOR - Geotechnical Engineer of Record |  | AOR - Architect of Record |  |  |  |  | SEOR - Structural Engineer of Record
|  | MEOR - Mechanical Engineer of Record |  | EEOR - Electrical Engineer of Record |  |  |  |  | CONT O/B - Contractor or Owner/Builder
|  | SP. INSP - Special Inspector |  | IOR - Inspector of Record |  |  |  |  | Test Lab – Engr. For the approved agency
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on F5: Describe each project stage, milestone, or interval for which one or more Verified Compliance Report is required. per CAC 7-141(i) and 7-151(f). A milestone or interval can include multiple stages.
Note on G6: GEOR = Geotechnical Engineer of Record
Note on H6: AOR = Architect or Record (often the Architect in Responsible Charge of the entire project)
Note on I6: SEOR = Structural Engineer of Record
Note on J6: MEOR = Mechanical Engineer of Record
Note on K6: EEOR = Electrical Engineer of Record
Note on L6: CONT = Contractor
Note on M6: IOR = Inspector of Record
Note on N6: SP INSP = Special Inspector Employed by Approved Inspection Agency
Note on O6: TEST LAB = Approved Testing Agency
Note on P6: Additional column may be added here. For large projects attachments may be required to identify all Verified Report Requirements
Note on F23: Aligns with Assembly Bill 2789
Note on F24: Aligns with Assembly Bill 2789

## G-IOR
SECTION G | Inspector of Record (IOR) Responsibility
Facility #: | Facility Name: | Project #:
INSPECTOR OF RECORD RESPONSIBILITIES. Per CAC 7-145: “The Inspector shall have personal knowledge, obtained by continuous inspection of all work of construction in all stages of its progress to ensure that the work is in accordance with the approved construction documents.” This includes applicable Codes, Referenced Standards, Listings and Manufacturer’s Installation Instructions applicable to the work shown in the approved construction documents. If a project has more than one inspector of record, the distribution of responsibilities for the work shall be clearly identified for each IOR per CAC 7-141(f). One IOR shall be designated as the ‘lead’ IOR per CAC 7-144(b). One IOR shall be assigned responsibility for “all other work” to make sure responsibility for the inspection of every part of the work is assigned.
INSPECTOR OF RECORD CAC 7-141, 7-145 & 7-151 | SCOPE OF INSPECTION |  | PERFORMED OFF-SITE
All other work
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## H-Plan Review
SECTION H | HCAI REVIEWED
Facility #: | Facility Name: | Project #:
NOTE: When a structural engineer has been delegated responsibility for a portion of this project his or her signature is also required.
Submitted By:
I have reviewed the approved construction documents for this project and all tests and special inspections required by Code are marked as “required” on this form.
Architect/Engineer of Record (Print Name) |  | Architect/Engineer of Record (Signature) | Date
Structural Engineer of Record (Print Name) |  | Structural Engineer of Record (Signature) | Date
FOR HCAI USE
TIO Program Reviewed by HCAI Plan Review Staff:
Note: HCAI plan review staff must provide verification that the TIO program has beeen "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. Field staff will issue subsequent "TIO Program Approval".
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## I-TIO Program Approval
SECTION I | TIO PROGRAM APPROVAL
Facility #: | Facility Name: |  | Project #:
This program is prepared and submitted for an OSHPD 1 project. OSHPD 1 projects include all construction and remodel projects for: general acute care hospitals, acute psychiatric hospitals, and general acute care hospitals providing only acute medical rehabilitation center services (2022 CBC 1224.1).
Samples of Test and Inspection Reports are NOT required for tests performed by laboratories approved through OPAA Program
All test and special inspection reports shall be submitted to the IOR, hospital owner, architect in responsible charge, and the structural engineer by the responsible approved agency and/or individual per CAC 7-149(a). The responisble approved agency and/or individual shall be employed by the health facility, owner, or governing board or authority per CAC 7-149(b).
Verified compliance reports shall be signed by the individual who performed the special inspection(s) as outlined in CAC 7-151 (c). All reports shall clearly state whether the tests or special inspections were performed in accordance with the HCAI stamped approved documents and whether the results indicate compliance with those documents per CAC 7-149 (a). All IORs performing special inspections shall hold the appropriate certification and equipment, and shall obtain approval from the design professional of record and HCAI prior to performing such work.
NOTE: This Test, Inspection, and Observation Report shall be approved by HCAI field personnel prior to start of construction.
Architect/Engineer of Record (Print Name) |  | Professional License # | Architect/Engineer of Record (Signature) | Date
FOR HCAI FIELD STAFF USE
TIO Program Approved by HCAI Field Staff:
Note: HCAI plan review staff must provide verification that the TIO program has been "Reviewed" prior to plan approval to confirm the applicability of the tests and inspections identified in the TIO program for work scope, building systems, and the construction materials shown in the design drawings. HCAI Field staff will issue subsequent "TIO Program Approval". If "Approved with Comments" is checked the following comments shall be resolved by the designer prior to proceeding with the related construction:
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A

## J-Changes
SECTION J |  | SUMMARY OF CHANGES TO THE TIO PROGRAM NOTE: Note all changes shall be approved as amended construction documents per CAC 7-153, or “concurred with” as non-material alterations per CAC 7-153(b), by HCAI prior to proceeding with the related work.
Facility #: | Facility Name: |  |  | Project #:
TESTING, INSPECTION, AND OBSERVATION PROGRAM NON-MATERIALLY ALTERING CHANGES BY THE ARCHITECT OF RECORD / ENGINEER OF RECORD IN RESPONSIBLE CHARGE |  |  |  |  | HCAI FDD CONCURRENCE (Initial/date)
A signature below indicates that the DPOR has verified the acceptance statements in Section I of this Form are applicable to any approved agencies/testing laboratories and special inspectors added.
REVISION NUMBER | SYNOPSIS OF CHANGE | Architect/Engineer of Record Signature (Initial/date) | Structural Engineer of Record Signature (Initial/date) | DATE of Effective Change
Note on D3: Do not enter anything on this row; project information is only entered on Section/Tab A
Note on D6: Enter a Revision Number for each change to the TIO Form
Note on E6: Brief description of the change to the form
Note on F6: Place initials in the box to indicate the architect or engineer in responsible charge has reviewed and approved the changes
Note on G6: Place initials in the box to indicate the structural engineer has reviewed and approved the changes (not required for changes which don't affect structural)
Note on H6: Effective date of the change

## Revison History
Revision number is shown at Section A, bottom right corner.
Version | Date | Description
R04.30 | 2023-01-20 | Updated for 2022 CBC
R04.31 | 2023-03-29 | Fixed buttons on tab E (error hiding rows).
R04.32 | 2023-04-20 | Added and Revised Med Gas Plumbing Tests B-P3 through B-P7.
R04.32 | 2023-04-20 | Revised language on Electrical On-Site Inspections C-E1 through C-E3
R04.33 | 2023-07-12 | Increased max number of stages to 50
R04.33 | 2023-07-12 | Revised title on items C-E2 and C-E3. Item C-E4 was added to tab C and removed from tab B
R04.34 | 2023-08-18 | Updated print titles to show column headings on each page
R04.35 | 2023-09-22 | Updated language for On-Site Inspections CE-2, CE-3, CE-4, and CE-6.
R04.36 | 2024-01-29 | Minor macro updates